Tender No:. 2024-25/Estate/2B/LNM-829

The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for the “supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricated Stand”. Bidders can submit their sealed offers/s at the following address by Email/Speed-Post/ Registered Post/ By-hand/courier before 05:00 PM on 10 January 2025.

Filing of Tender:

Option 1: Physical submission of offers (hard copy) in sealed envelopes.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the institute in person/ Speed-Post/ Registered Post/ By-hand/courier of the Institute after marking due entries in the Receipt Book available with the Security Officer at the main gate.

The tender subject and reference number must be mentioned on the envelope.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Option 2: Password-protected online submission via Email

Password-protected offers can be submitted by the bidders via email at the below-mentioned email IDs.

tender-document@lnmiit.ac.in (password-protected document)

tender-password@lnmiit.ac.in (password only)

The tender subject and reference number must be mentioned in the subject line of the emails.

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory, are required to be submitted in two separate envelopes/emails.

Envelopes/Emails should be duly marked as follows:

- Technical bid for the “supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricated Stand”.

- Commercial Bid for the “supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricated Stand”.

Both Envelopes/files should be enclosed/attached in a single envelope/email bearing the heading “Bid for the “supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricated Stand (Tender No. : 2024-25/Estate/2B/LNM-829) ”.

Bids are liable to be rejected:

- If the above-mentioned bid submission procedure is not followed.

- Incomplete and non-conforming bids.

- Arbitration: All disputes and differences arising between the two parties in connection with this order shall be mutually settled as far as possible, failing which, all such disputes shall be referred to arbitration and settlement under the provision of the Arbitration and Conciliation Act, 1996 and as amended from time to time or any such law for the time being prevailing in India. The venue of such arbitration shall be Jaipur.

Technical Bid: (in a separate sealed envelope/via email)

# Bid for supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricated Stand

# (Tender No. : 2024-25/Estate/2B/LNM-829)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turnover for the last three years to be mentioned. (Copy to be enclosed)

- List of the client to whom the vendor has delivered the goods or provided the services in the past.

- Specification as mentioned below, shall be provided as per the details given below:

## Scope of work

- The scope of work will cover the supply/service/SITC of given  items at LNMIIT Jaipur campus.

- The Vendor is required to submit the complete documentation of the supplied item after delivery.

- SITE CONDITION:

Before quoting, the contractor must visit the site to inspect the work and shall fully acquaint himself about the conditions and scope of work with regards to accessibility of site required for the satisfactory execution of work. No compensation on account of any site difficulties will be entertained at a later date, after the award of the works.

Technical specification:

| S/No | Specification | Parameter requirements |
| --- | --- | --- |
|  | Make | Numeric |
|  | Model | Numeric Onfiniti |
| 1. | UPS Capacity | 10 kVA |
| 2. | Technology | a. True online double conversion b. IGBT based rectifier & inverter c. Inbuilt PRS kit for Parallel Option in future |
| 3. | Input Parameters: |  |
| a. | Voltage | 230 VAC, 1 Phase |
| b. | Voltage Range | 110V to 300 VAC based on load level |
| c. | Frequency | 50 Hz |
| d. | Power Factor at rated load | Unity at full load |
| e. | Current Harmonic Distortion | Less than 10% |
| 4. | Output Parameters: |  |
| a. | Voltage | 220/230/240 VAC +/ - 1%, 1 Phase |
| b. | Frequency | 50 Hz +/- 0.25 Hz (in Battery Mode) +/- 6% (in Sync) |
| c. | THD v | < 2 % for Linear Load ; < 5 % for Non Linear Load |
| d. | Overload rating | 105 to 109 % - 10 min ; 110 to 129 % - 60 sec ; 150 % - 10 seconds |
| e. | Output waveform | Pure sinewave |
| f. | Crest Factor | 3 : 1 |
| g. | Output Power Factor | 0.9 |
| h. | Over all Efficiency | >93% without Transformer |
| 5. | Battery Parameters: |  |
| a. | Batteries Type ( 12V VRLA) | Sealed Maintenance Free Batteries ( Exide ) |
| e. | Backup Time | 30 Mins. |
| f. | DC Voltage | 192 VDC |
| h. | Battery Rack | Battery Rack / Stand |
| i. | Transfer time | UPS to Battery Mode : 0 ms |
| j | Three Stage Charger | Constant Voltage / Constant Current / Float Charging with Temperature Compensated Charger |
| k | Charging Capacity | 10 % of the Battery AH Capacity |
| 6. | Bypass: |  |
|  | Static Bypass | Required (Inbuilt) |
|  | Transfer time | < 4 ms in Sync Mode |
|  | Bypass parameter configurable via front panel | Required |
|  | Manual Bypass | Required (Inbuilt) |
| 7. | LCD Display / Alarm / Protection |  |
| a. | Metering Data |  |
|  |  | Input Voltage |
|  |  | Input Frequency |
|  |  | Output Voltage |
|  |  | Output Frequency |
|  |  | Output Power in Watts |
|  |  | Output Current |
|  |  | Load Level in % |
|  |  | Battery Voltage |
|  |  | Battery Level |
|  |  | Temperature |
|  |  | Event Log |
|  |  | Battery Test |
| b. | Status Information Data |  |
|  |  | Normal |
|  |  | Bypass |
|  |  | Battery |
|  |  | Fault |
|  |  | Converter Mode |
|  |  | Eco Mode |
|  |  | Bypass Mode |
|  |  | Battery Mode |
| c. | Fault / Waring Indication |  |
|  |  | Over Load |
|  |  | Charger Fail |
|  |  | Inverter Fault |
|  |  | Over Temperature |
|  |  | Short Circuit |
|  |  | DC low / High |
|  |  | Output Low / High |
|  |  | Fan Fail |
|  |  | Battery Disconnected |
| d. | Protection Required | Input High / Low |
|  |  | Over Load |
|  |  | Short Circuit |
|  |  | Over Temperature |
|  |  | Battery Over Charge |
|  |  | Battery Deep Discharge |
| e. | Audible Alarm | Battery Mode |
|  |  | Low Battery |
|  |  | Fault |
|  |  | Over Load |
|  |  | Bypass Mode |
| 8. | Other Features: |  |
| a. | Communication Port | RS 232 & USB |
| b. | Cold Start | Required |
| c. | Auto Restart | Required |
| d. | EPO | Required |
| e. | Generator Compatibility | Required |
| f. | SNMP Card | Optional |
| g. | Operating Temperature | 0 to 45 Deg C without derating |
| h. | Storage Temperature | 0 to 60 Deg C |
| i. | Humidity | upto 95 % |
| j. | Altitude | < 1000 meters |
| 9. | Connection |  |
|  | Input | Terminal Block |
|  | Output | Terminal Block |
|  | Battery | Terminal Block |
| 10. | Credential / Reports |  |
|  | ISO 9001 2015 | Copies Required |
|  | ISO 14001 2004 | Copies Required |
|  | ISO 45001: 2018 | Copies Required |
|  | BIS Certificate | Copies Required |
|  | JIS 8702C for battery | Copies Required |
|  | Manufacturing facility | a. Make in India. b. OEM Minimum 10 Years presence in India. |
|  | Service facility | UPS manufactures should have not less than 200 service centers accross India. |
|  | Turn Over | Vendor should have turn over more than 300 crores |
| 11. | Warranty /After Sales Support |  |
|  | Service Support | Directly from OEM for UPS & Batteries Both |
|  | Warranty | Onsite 24 Months on UPS & Batteries |
|  | Numeric Authorized service center | Local Authorized service center in Jaipur |
|  | Authorized Supplier Certificate | Numeric |

Commercial Bid: (in separate sealed envelope/password protected file in Email)

Supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricated Stand

# Bid for (Tender No. : 2024-25/Estate/2B/LNM-829)

| S. No. | Particulars | Make | Qty. | UOM | Rate | Amount |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Supply, Instruction, testing and commissioning of 10 KVA Single Phase online UPS System with two-year warranty | Numeric/APC/Socomec | 1 | Nos. |  |  |
| 2 | SMF UPS Battery 26 ah/12V with Copper Interlinks Cables & MS Fabricate Stand | Exide/ Amaron | 16 | Nos. |  |  |
|  | Total |  |  |  |  |  |
|  | GST_______ |  |  |  |  |  |
| TOTAL (including taxes) |  |  |  |  |  |  |

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should	include everything (packing, forwarding, transit insurance, transportation, loading /unloading, installation etc.). Loading/unloading up to 50 mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- The bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only.

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

- All charges applicable shall be clearly mentioned in the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

All charges applicable shall be clearly mentioned with the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

Signature with seal