# Tender No:. 2024-25/Estate/2B/LNM-769

The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand”. Bidders can submit their sealed offers/s at the following address by Email/Speed-Post/ Registered Post/ By-hand/courier before 05:00 PM on 10.01.25 (Last date of bid submission).

Filing of Tender:

Option 1: Physical submission of offers (hard copy) in sealed envelopes.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the institute in person/ Speed-Post/ Registered Post/ By-hand/courier of the Institute after marking due entries in the Receipt Book available with the Security Officer at the main gate.

The tender subject and reference number must be mentioned on the envelope.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Email: directoroffice@lnmiit.ac.in

Option 2: Password-protected online submission via Email

Password-protected offers can be submitted by the bidders via email at the below-mentioned email IDs.

tender-document@lnmiit.ac.in (password-protected document)

tender-password@lnmiit.ac.in (password only)

The tender subject and reference number must be mentioned in the subject line of the emails.

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory, are required to be submitted in two separate envelopes/emails.

Envelopes/Emails should be duly marked as follows:

- Technical bid for the: :  Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand.

- Commercial Bid for the: Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand.

Both Envelopes/files should be enclosed/attached in a single envelope/email bearing the heading “Bid for the Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand  (Tender No. : 2024-25/Estate/2B/LNM-769) ”.

Bids are liable to be rejected:

- If the above-mentioned bid submission procedure is not followed.

- Incomplete and non-conforming bids.

- Arbitration: All disputes and differences arising between the two parties in connection with this order shall be mutually settled as far as possible, failing which, all such disputes shall be referred to arbitration and settlement under the provision of the Arbitration and Conciliation Act, 1996 and as amended from time to time or any such law for the time being prevailing in India. The venue of such arbitration shall be Jaipur.

Technical Bid: (in a separate sealed envelope/via email)

Bid for the Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand

(Tender No. : 2024-25/Estate/2B/LNM-769)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turnover for the last three years to be mentioned. (Copy to be enclosed)

- List of the client to whom the vendor has delivered the goods or provided the services in the past.

- If a vendor firm is applying for the first time please submit the last three years' purchase orders, and work completion certificates.

- Specification as mentioned below shall be provided as per the details given below::

Scope of work, Technical data sheet and Specification of the item/s

Scope of work: 	Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand

Specifications:

| S.N | Description | Specification (Minimum) |
| --- | --- | --- |
| 1. | General Specifications |  |
| i | Modular UPS Topology | Online Double Conversion VFI SS 111 |
| ii | Architecture of the UPS | Modular, scalable, redundant based Power Modules of 5KVA to 10KVA |
| iii | Power Cabinet Capacity | 30KVA |
| iv | Real & Active power in Each Power Module | Output Power Factor should be Unity (KVA=KW) |
| v | Redundancy in Control Panels/ Board | Multiple Control panel (Mandatory) |
| vi | Redundancy in Power Modules | All Power Modules should deliver power to load with no standby mode. |
| vii | Hot Plug- Hot Swap | In redundant configurations the UPS must be able to supply and protect the load, also during the replacement of faulty module and no bypass switch is needed |
| viii | In/Out phase Configuration | Three phases |
| ix | Neutral | Neutral Passing through |
| x | Redundancy in Battery Bank | Supplier had to provide two Parallel Bank for maintaining the redundancy in Battery Bank |
| xi | Bypass type | Static and electro mechanic (Maintenance Bypass) |
| xii | Transfer time | Zero as per IEC 62040-3 |
| 2. | Input |  |
| i | Nominal Voltage | 400 V three phase |
| ii | Voltage range | -15% +15% |
| iii | Frequency | 45-65 Hz |
| iv | THDIin | < 3% al 100% of nominal load |
| v | Power Factor | > 0.99 @ 50% load |
| 3. | Output with mains (AC-AC) |  |
| i | Nominal voltage | 400 V three phase |
| ii | UPS should have other Input & Output Phase Onsite configuration facility also | 1Phase (I/P) /1Phase (O/P) or 3Phase (I/P) /1Phase (O/P) |
| iii | Nominal power | 30KVA |
| iv | Active power | 30KW |
| v | Voltage variation (static) | ± 1% |
| vi | Voltage variation (dynamic 0-100%; 100-0%) | ± 1% |
| vii | THDv on nominal power | < 1 % |
| viii | Frequency | 50 Hz +/- 0.1% |
| ix | Frequency tolerance | Synchronized with input frequency or ± 1% free run |
| x | Current Crest Factor | 2.5:1 accordingly with IEC EN62040-3 |
| xi | Overall Double Conversion Efficiency | Upto 96% |
| xii | Eco mode | > 98% |
| xiii | Overload capability: | Minimum 115% load rate with no bypass intervention for 5 min; Minimum 135% load rate with no bypass intervention for 30 seconds |
| 4. | UPS Power Module |  |
| i | Each Power Module will be composed by following functional blocs | Inverter, Booster, Battery Charger, Rectifier/PFC, Automatic Bypass |
| 5. | Battery |  |
| i | Type | Lead Acid, sealed, free maintenance VRLA |
| ii | Nominal UPS Battery Voltage | 240 Volt DC |
| iii | Backup Time Required is of 2 Hrs | Minimum 48000 VAH for 120 min backup on 15KVA load (Vendor should develop redundancy in Battery Bank also i.e 60mins + 60 mins) |
| iv | Battery charger type | Each power module should have individual battery charger |
| v | Charging Cycle | Intelligent with boost charge and advanced management |
| vi | Battery Management | Battery test either automatically or upon the user’s request |
| vii | Battery Cabinet | MS Rack with Circuit Breaker |
| 6. | Environmental specs |  |
| i | Noise level @ 1m | 50 - 65 dBA |
| ii | Working temperature range | from 0°C to +40°C |
| iii | Humidity range | 20-95% not condensing |
| iv | Protection degree | IP21 |
| 7. | Others |  |
| i | Remote Monitoring | Through SNMP Card (To be provided) |
| ii | UPS OEM Certificates | Should have ISO 9001, 14001 & 45001 |
| iii | Product Enviornmental Profile | UPS Model should be PeP Certified (Must) |
| iv | Product Standards | EN 62040-1, EN 62040-2, EN 62040-3 |
| v | Product Marking | UPS should be UE /CE approved |
| vi | SMF Batteries Brand | Exide/ Quanta (Amaron) |
| vii | UPS Brand | Numeric (Legrand), ABB, Socomec |
| 8. | Warranty on UPS & Batteries |  |
| i | Warranty on UPS & Batteries | Onsite 24 months on UPS & 2 years on SMF Batteries from date of Installation or 24 months on UPS & SMF Batteries from date of delivery, whichever happens earlier |

| S.No. | Particulars | Make | Qty. with UOM |
| --- | --- | --- | --- |
| 1. | Supply, Installation, Testing & Commissioning of 30 KVA Three Phase Online Modular UPS System with Two years warranty | Numeric/APC /Socomec/ABB | 1 Nos |
| 2. | 12V/100 AH SMF UPS Battery with 120 min. Backup | Exide/Amaron | 40 Nos. |
| 3. | Battery MS Fabricated Stand with Copper Interlink cables |  | 1 nos. |

Commercial Bid: (in separate sealed envelope/password protected file via email)

Bid for Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand

(Tender No. : 2024-25/Estate/2B/LNM-769)

| S. No. | Particulars | Make | Qty. | UOM | Rate | Amount |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Supply, Installation, Testing & Commissioning of 30 KVA Three Phase Online Modular UPS System with Two years warranty | Numeric/APC /Socomec/ABB | 1 | Nos. |  |  |
| 2 | 12V/100 AH SMF UPS Battery with 120 min. Backup | Exide/Amaron | 40 | Nos. |  |  |
| 3 | Battery MS Fabricated Stand with Copper Interlink cables |  | 1 | Nos. |  |  |
| 4 | Transportation charges |  | 1 | Nos. |  |  |
|  | Total |  |  |  |  |  |
|  | GST_______ |  |  |  |  |  |
| TOTAL (including taxes) |  |  |  |  |  |  |

- Taxes like GST should be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should	include everything (packing, forwarding, transit insurance, transportation, loading /unloading, installation etc.). Loading/unloading up to 50 mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- The bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only.

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

- All charges applicable should be clearly mentioned in the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

Signature with seal