THE PROPOSED CONSTRUCTION

OF

LNMIIT INTERNATIONAL CENTRE FOR ARTIFICIAL INTELLIGENCE

TENDER DOCUMENT

FOR

DG WORKS

THE LNM INSTITUTE OF INFORMATION TECHNOLOGY,

RUPA KI NANGAL, VIA JAMDOLI, JAIPUR, RAJASTHAN.

Index

| Sno. | Description | Page No. |
| --- | --- | --- |
| 1. | Notice Inviting Tender | 3 |
| 2. | Instruction to bidders | 4 |
| 3. | Eligibility Criteria | 6 |
| 4. | Scope of work | 10 |
| 5. | General Terms & Conditions | 13 |
| 6. | Technical Specifications for D.G Sets | 17 |
| 7. | List of Approved makes | 38 |
| 8. | Schedule of quantities | 39 |
| 9. | Affidavit | 45 |
| 10. | Proforma EMD/Performance bank guarantee/Security deposit | 46 |
| 11. | Price bid | 49 |

Notice Inviting Bid

(Competitive bidding)

NIT no.: LICAI/NIT/002

The Director on behalf of THE LNM INSTITUTE OF INFORMATION TECHNOLOGY, JAIPUR (“LNMIIT”) having its office at Rupa ki Nangal, Via Jamdoli, Jaipur invites Item rate tender from Eligible firms/agencies for the following works thru online/hard copy submission under two bid system:

Name of the Project: Construction of LNMIIT International Centre for Artificial intelligence (LICAI) (G+5) at Jaipur.

Sub Head: DG Set works.

Detail of the Tender bid:

Earnest Money: Rs. 4,68,000.00

Period of Completion: 3 Months.

Mobilization time - Nil

Date of Issue of Bid: 24.02.2025

Date & Time of Pre-Bid Meeting:.1030 hours 10.03.2025

Last date & time of submission of bid document: 24.03.2025

Name: GP.  Capt. Pushpendra Singh (Chief Administrative Officer)

Phone No.: 0141-3526101

Email id: cao@lnmiit.ac.in

Director

LNMIIT

Instructions for the Bidder

- This Notice Inviting Tenders (Part-1,2,3 & 4) i.e. Eligibility criteria for the bidder, Scope of work, Terms & conditions, Comprehensive warranty, Defects liability period, Comprehensive Maintenance for 5 years, General terms & conditions, General technical conditions, technical specifications, List of approved makes, Affidavit, Proforma for Bank guarantee, Price bid & Drawings shall form the TENDER DOCUMENTS.

- The bid document shall be submitted in two envelopes consisting of the following:

Envelope 1: Bid document duly signed and stamped by the authorised signatory along with the EMD as specified.

Envelope :2: Price Bid.

Price bid envelope i.e envelope 2 will be opened only of those bidders who successfully meet the eligibility criteria.

- The Contractors are to pay the amount of earnest money as specified in the tender notice separately along with the Tender. Tenders for which earnest money deposit has not been received separately shall be returned unopened/not to be considered for further processing.

- The Contractor should certify that he has studied the Work at site and acquainted himself with the position regarding construction, materials & labour required for the work.

- Should the Contractor notice any discrepancy or error in any statement made, he shall immediately bring to the notice of the LNMIIT-Project Manager of LNMIIT, Jaipur (project.manager@lnmiit.ac.in) and obtain clarifications before submitting the tender.  The tender shall be recorded as such in the covering letter to the tender, failing which the Owner shall have right to ask the Contractor to execute the Work according to the statement made in the tender, without any compensation.

- The Rates should be quoted in figures and words, and the respective amounts or total shall be given by each TENDERER. In case of any difference in rates in figures / words, those given in words, shall hold good as quoted rate and in case of any difference in rates and Total amount, quoted Rates shall hold good.

- The TENDERS shall remain valid for acceptance for 60 days from the last date of Submission.

- The successful TENDERER shall be intimated about the Award of Work and the Earnest Money Deposits of other TENDERERS shall be returned without any interest on the amount deposited.

- The LNMIIT reserves the right to reject any / all TENDERS without assigning any reason and shall not be bound to accept the lowest or any other TENDER.

- TENDER not accompanied by the requisite EARNEST MONEY DEPOSIT in the specified form or accompanied with the conditional offer are liable to be summarily rejected.

- The Bidder should stamp and sign the document in order to ascertain that he complies with all the specifications and terms and conditions mentioned in the Bid.

- Earnest money deposit will be paid online or thru Demand draft or by online bank transfer to the following bank account:

Account Name         : “ The LNM Institute of Information Technology”

Account No.     :       001201038168

Bank                    :       ICICI Bank Ltd.

Branch         :     C-Scheme, Jaipur

IFSC Code     :       ICIC0000012

Account type    :       Saving account

The acknowledgement of the EMD should be mailed to the Chief Finance Officer on the email: cfo@lnmiit.ac.in.

- Co-ordination with other agencies / contractors appointed directly by the owner:

The Successful bidder shall co-ordinate and provide facilities for the contractors appointed by the LNMIIT.

In addition to the above Clauses all requirements will have to be implemented by the Bidder for all persons employed by him working on the Site including monitoring to ensure implementation etc., employed directly by the Owner.

- The tender of any Contractor not complying with any of the above instructions 1 to 12 may be rejected.

I / We have carefully read the above said instructions have understood the same and shall comply with the same.

Place : 							Signature of the Contractor

Date:								With seal & address

Name of the Contractor: -

Contact No.

e-mail id:

Part-1

Eligibility Criteria for the OEM (D.G Set Manufacturer)

| Sno. | Parameter | Documents to be submitted by Bidder |
| --- | --- | --- |
| 1 | Earnest Money Deposit: | The bidder should submit and EMD of Rs. 4,68,000/- (Four lacs sixty-eight thousand only) |
| 2. | OEM/D.G Set Manufacturer Turnover | The OEM should submit the CA Certified turnover document for the Financial Turnover of Bidder for last three Financial Years i.e FY 2021-22, 2022-23 and 2023-24 . |
| 3. | OEM Authorized Certificate | The OEM, shall submit an undertaking whereby the bidder declares itself is OEM on his letterhead duly signed and stamped |
| 4. | Experience criteria & Past performance for the bidder | To qualify, each bidder should have supplied /executed similar category product/work i.e SITC of the D.G sets in any Govt. Department/PSU/ Public Listed Company in last five years with: One works of minimum value of Rs. 1,60,00,000/- Or Two works of minimum value of Rs. 95,00,000/- Or Three works of minimum value of Rs. 65,00,000/- Requirements: - Completion certificates mentioning order number and order value issued by the relevant competent Authority |
| 6. | Experience Criteria & Past Performance for the OEM/D. G Set manufacturer | The OEM shall have manufacturing experience of D.G Sets for a minimum of 15 years. The Bidder should submit valid documentary evidence in support of the same. |
| 7. | Necessary Qualifying Criteria for OEM/D.G. Set Manufacturer | To qualify, the OEM/ D.G Set Manufacturer should comply to following conditions: 1) Manufacturing and Testing Facility, R&D Centre and dedicated training centre to train its personnel in India. 2) Domestic Production capacity of the factory in India shall not be less than 1000 D.G Sets per annum. 3) The Manufacturer shall have Service Centers in at least 25 Nos town/cities including at least 15 Nos state capitals in India. 4) The D.G Set Manufacturer shall furnish an undertaking regarding availability of spares for entire life of the D.G sets i.e 15 to 20 years 5) The D.G Set Manufacturer shall furnish an undertaking that: a) D.G Set tests and safety features confirms to relevant updated Indian standards b) Quality standards shall confirm to IS/ISO— 9001:2015 c) The Fire Rating of the D.G Sets shall be as per National Building Code-2016 d) The downtime of the D.G Set shall not be more than 8 hrs (average) in case of minor faults and 7 days (average) in case of major faults. 6) Details of Tollfree Number, Emai-Id for lodging complaints shall be provided. |
| 8. | GST number | The bidder should attach GST number detail mandatorily |
| 9. | PAN Card | The bidder should attach PAN card detail mandatorily |
| 10. | BOQ Compliance | The Bidder should stamp and sign the document in order to ascertain that he complies all the specifications and terms and conditions mentioned in the Bid |
| 11. | Location of the nearest Service Centre | The Bidder has to provide the Address of the Service Centre along with Contact Number |
| 12. | ISO 9001:2015 Certificate | The Bidder should submit the valid ISO 9001:2015 Certificate of the Bidder/OEM |
| 13. | Affidavit as per Annexure-1 | The Bidder should submit the Affidavit as per Annexure-1 |

Part-2

Scope of Work:

- This work covers supplying,  DG Set ,Installation ,Testing and Commissioning of D.G sets  complete, all preparatory work & putting into operation of D.G Sets including comprehensive maintenance for 5 years including one year of defects liability period.

- Location: The work shall be carried out in the Building of LNMIIT International Centre for Artificial intelligence (LICAI) (G+5) at Jaipur

- The work shall be executed as per CPWD General Specifications for D.G works, Part-VII 2013, as amended upto date and as per directions of Project manager. These additional specifications/ conditions are to be read in conjunction with above and in case of variations; specifications given in these additional conditions shall apply. However, nothing extra shall be paid on account of these additional specifications and conditions, as the same are to be read along with the schedule of quantities for the work.

- The tenderer should in his own interest visit the site and get familiarized with the site conditions before tendering.

- The work shall comprise of entire labour including supervision and all materials necessary to make a complete installation and such tests and adjustments and commissioning as may be required by the department. The term complete installation shall not only mean major items of the plant and equipment’s covered by specifications but all incidental sundry components necessary for complete execution and satisfactory performance of installation with all layout charts whether or not those have been mentioned in details in the tender document in connection with this contract.

- All debris/Malba resulting due to work shall be removed on daily basis and completion of the work shall only be accepted after the site has been cleaned of all malba.In case contractor fails to comply the same shall be got removed by the other agency at the payment shall be recovered from the bill of the contractor.

- Minor building works necessary for installation of equipment’s, foundation, making of opening in walls or in floor and restoring to their original conditions, finish and necessary grouting etc. as required.

- The contractor shall be bound to execute such additional items which can be termed as logical, essential and necessary (even though not listed in schedule of work) for the effective execution of the work in totality.

- Maintenance (routine and preventive) DLP for Two year from date of completion and handing over to department/Client.

- Inspection and testing: All routine tests confirming to be relevant shall be carried out and the test reports shall be submitted to Project Manager. The copies of all documents of routine and type test certificates of the equipment, carried out at the manufacturer’s premises shall be furnished to the Project Manager and consignee at the time of delivery of material at site. After completion of the work in all respects the contractor shall offer the installation for testing and operation.

12) COMPLIANCE WITH REGULATIONS AND INDIAN STANDARDS: All works shall be carried out in accordance with relevant regulation both statutory and those specified by the Indian Standards related to the works covered by this specification. In particular, the equipment and installation will comply with the following:

(i) 	BS: 5514 Specification for reciprocating internal combustion engine.

(ii) 	BS:5000 Rotating electrical machines of particular type or for particular applications.

(iii) 	IS: 1239 (Part-I & II) : Mild steel tubes and fittings

(iv) 	IS: 1651: Stationary cells and batteries lead acid type (with tubular positive plates).

(v) 	IS: 9224: Specification of low voltage fuses, General purpose.

(vi) 	IS: 4540: Mono-crystalline semi-conductor rectifier assemblies and equipment.

(vii)	IS: 5: Colours for ready mixed paints.

(viii)	IS: 4722: Rotating electrical machines

(ix)	IS: 1248: Specification for electrical indicating instruments.

(x)	IS: 10000: Methods of tests for internal combustion engines.

(xi)	IS: 10002: Specifications for performance requirements for constant speed

compression ignition (Diesel) engine for general purposes (above 20 KW)

(xii)	IS: 2147 : Degree of protection provided by enclosure for low voltage switchgear and control gear.

(xiii)	IS: 1600 : Code for type testing of constant speed IC engines for general purposes.

(xiv)	IS: 1601 : Performance of constant speed IC engines for general purposes.

xv)	ASME Power : Internal combustion engines.

(xvi)	Test Code PTC-17 : Codes of Diesel Engine Manufacturer's Association U.S.A

13)	Installation:

The installation work shall conform to Indian Electricity act and Indian Electricity Rules as amended upto the date of installation. The fuel oil installation shall meet all statutory requirements of Govt. of India as amended up to the date of installation. Any approval required from statutory authorities shall be obtained by the contractor. Nothing in this specification shall not be the limiting factor to relieve the contractor of their responsibilities.

The equipment’s furnished under this specification have to operate in a tropical climate and shall be given tropical and fungicidal treatment as per relevant specification.

14) Maintenance:

a. Sufficient trained and experienced staff & Engineer shall be made available to meet any exigency of work during the guarantee period of minimum two year from the handing over of the installation.

b. Routine as well as preventive maintenance for one year from the date of taking over the installation shall be carried out and the record of the same shall have to be maintained.

c. Comprehensive maintenance period of 5 years for the successful bidder will begin after the  completion of  DLP.

15) Training:

The scope of the work includes on-the-job technical training of two persons at site. Nothing extra shall be payable on this account.

16)  Test Certificate:

As regards the type tests in case these have been done earlier by OEM for similar design/ type, same if produce shall be acceptable. In case, same is not done earlier, these will have to be done for one of the transformers of the present lot.

Part-3	Terms & Conditions for comprehensive warranty/defects liability period of one year and comprehensive maintenance for 5 years.

1) The Contractor shall regularly examine, lubricate and adjust the equipment and generally carry out planned maintenance in a systematic and controlled manner.

2) The Contractor shall repair or replace any parts detail which are found to be defective.

3)  All equipment covered in the contract are included in the comprehensive maintenance.

4) The contractor will assign a representative who will periodically visit the site once a month and will be available for consultation in any matter relating to the maintenance of DG Sets.

5) The work shall be carried out as General Specifications for D.G Sets-2013, Part-VII and amended upto date and the entire satisfaction of the Project manager.

6) The tendered rates shall be deemed to include all services covered under this contract and no extra payment will be made on this account.

7) Any accident that occurred due to negligence will be the entire responsibility of the contractor.

8) The time allotted for attending the complaints is 24 Hours and if the complaints are not done within 24 hours of the registration, a recovery @ Rs. 500/- per day shall be made against the contractor.

Part-4

General Terms & Conditions

1)  The intending bidder must read the terms and conditions of the bid carefully. He should only submit his bid if he considers himself eligible and he is in possession of all the documents required.

2) Information and Instructions for bidders posted shall form part of bid document.

3) The LNMIIT-Jaipur reserves the right to reject any prospective bid at any point of time, if the documents provided by the bidder appear to be fake or any false information is provided by the bidder.

4) The intending contractor is advised to visit the site of work, of his own, to acquainting himself regarding site details etc. prior to quoting the tender.

5) The time allowed for carrying out the work will be 90 days from the date of the contract order. If the Bidder fails to complete the work within 90 days from the date of contract order and the reason for delay is not found reasonable by the Project Manager, LNMIIT, he will be charged with @ Rs 5000/- per week. No fine will be imposed if the reason for the delay is found reasonable by the Project Manager.

6) Payment Terms:

a)  Serial no. “1.1 & 1.2” of the Price bid: 10 % of the quoted cost  after the award of the work as a advance .65 % of the quoted  price will be paid after successful  delivery at site. 20 % quoted price will be paid after successful completion of Installation Testing and Commissioning. Rest 5% of quoted price will be paid after successful completion of DLP .

b)   Serial no. “2.1 & 2.2 ” of the Price bid: 95% of the quoted cost will be paid to the Bidder on the successful Installation  testing and commissioning. Rest 5% of quoted price  will be paid after successful completion of DLP .

c) Serial No.  “3.1 & 3.2” of the Price bid: Payment to the bidder for this stage shall be as follows:

| Sno. | Payment schedule | % (Percent) |
| --- | --- | --- |
| 1 | 1st Year | 10.0 |
| 2 | 2nd Year | 15.0 |
| 3 | 3rd Year | 20.0 |
| 4 | 4th Year | 25.0 |
| 5 | 5th Year | 30.0 |

7) Intending bidders are advised to inspect and examine the site and its surroundings and satisfy themselves before submitting their bids as to the nature of the ground and sub-soil (so far as is practicable), the form and nature of the site, the means of access to the site, the accommodation they may require and in general shall themselves obtain all necessary information as to risks, contingencies and other circumstances which may influence or affect their bid. The bidder shall be deemed to have full knowledge of the site whether he inspects it or not and no extra charge consequent on any misunderstanding or otherwise shall be allowed. The bidders shall be responsible for arranging and maintaining at his own cost all.

8) It is required that each Bidder/Contractor (including their respective officers, employees and agents) adhere to the highest ethical standards, and report to the Director-LNMIIT all suspected acts of fraud or corruption or Coercion or Collusion of which it has knowledge or becomes aware, during the tendering process and throughout the negotiation or award of a contract.

9) Performance Guarantee:

a) The contractor whose bid is accepted will be required to furnish a performance guarantee of 5% (Five Percent) Serial no. “1 (1.1 +1.2 ). Serial No. 2 (2.1 + 2.2” of the Price bid )   of the bid amount valid till the successful completion and  handing over of the complete work thin 20 days of the issuing of contract order. This guarantee shall be in the prescribed form mentioned in the Bid document. The performance Guarantee shall be released after 30 days of  successful completion and handing over complete work .

b) In addition to the above the successful bidder should furnish a performance guarantee of 5% (Five percent) of bid amount Serial No. 3 (3.1 + 3.2) of the Price bid) prior to the commencement of the comprehensive maintenance period of 5 years valid for 66 months. This comprehensive maintenance period will begin after the successful handover of the work.

The performance Guarantee in respect to Comprehensive Maintenance  will be released after 45 days from the completion of the Comprehensive Maintenance Period.

This guarantee shall be in the form of Insurance Surety Bonds, Account Payee Demand Draft, Fixed Deposit Receipt or Bank Guarantee from any of the Commercial banks in accordance with the prescribed form as provided in the bid. In case, the Bidder fails to deposit the said Performance Guarantee within the period as mentioned above including the extended period, if any, the Earnest Money deposited by the Bidder shall be forfeited automatically without any notice to the Bidder. The earnest money deposited along with the bid shall be returned after receiving the aforesaid performance guarantee.

10) Rates: The rates quoted by the tenderer, shall be firm and inclusive of all taxes (including works GST, labour cess), duties, levies, octrori etc. and all charges for packing forwarding, insurance, freight and delivery, installation, testing, commissioning etc. at site including temporary construction of storage, risks overhead charges, general liabilities/obligations and clearance required if any.

11) The Contractor has to carry out comprehensive, routine and preventive maintenance as per manufacturer’s standard for a period of minimum 12 months from the date of handing over. Nothing extra shall be paid on this account.

12) GUARANTEE: All equipment’s shall be guaranteed for a period of minimum 12 months, from the date of taking over the installation by the department/Client against unsatisfactory performance and/or breakdown due to defective design, workmanship or material. The equipment or components, or any part thereof, found defective during guarantee period shall be forthwith repaired or replaced free of cost, to the satisfaction of the Project Manager. In case it is felt by the department that undue delay is being caused by the contractor in doing this, the same will be got done by the department at the risk and cost of the contractor. The decision of the Project manager in this regard shall be final & binding on the contractor.

13) The successful tenderer should furnish well in advance three copies of detailed instructions and manuals of manufacturers for all items of equipment’s regarding installation, adjustments, operation and maintenance i/c preventive maintenance and troubleshooting together with all the relevant data sheets, spare parts, catalogue and workshop procedure for repairs, assembly and adjustments etc all in triplicate.

14)   Dispute Resolution: If any dispute with regard to the terms of this Contract shall be handled through Arbitration, as per the following terms, between them:

(I) THAT, the parties agree that any dispute or difference whatsoever arising between them out of/under or in connection with or relating to the existence, meaning, scope, validity, termination, breach, or any other effect flowing from the Contract shall be referred to a Sole Arbitrator, as appointed under clause (IV) herein below;

(II) AND THAT, the parties agree that in respect of those matters, as are not defined in the terms and conditions of this Dispute Resolution Clause, or anywhere else in the Contract, the same shall be decided and settled by the Sole Arbitrator, in accordance with the Arbitration and Conciliation Act, 1996 and the amendments thereof as in operation on the date of execution of the Contract;

(III) AND THAT, the parties agree that the place of Arbitration shall be at Jaipur, Rajasthan;

(IV) AND THAT, whenever the parties decide to resort/resolve to Arbitration for dispute

resolution, the Director, LNMIIT shall be the authority to appoint the Sole Arbitrator and such appointment shall be binding on both the parties:

Provided that before approaching Director-LNMIIT for appointment of Sole Arbitrator, the parties shall make a sincere attempt to resolve their dispute, within a time period of 3 months, through mutual conciliation/ negotiations. The sole arbitrator shall not be an employee of any of the party to this tender.

(V) AND THAT all costs relating to the Arbitration proceedings shall be borne equally by both parties.

(VI) AND THAT, the parties agree that the language for making all submissions and evidence will be presented in ENGLISH during the proceedings.

(VII) AND THAT, it is agreed between the parties that they shall extend their fullest support and co-operation to the Sole Arbitrator and not seek adjournment of the Arbitration proceedings, without explaining the reasons therefore, in writing, in advance, for seeking of such adjournment, and further that there shall not be more than two such adjournments granted, even when there exists a valid reason for seeking such adjournment. And, it is further agreed that the parties should cooperate in completing the arbitration process and the broader dispute resolution within 6 months or at most with an extension, on mutual consent, of another 6 months;

(VIII) The sole Arbitrator shall record, in writing, the arguments of the two parties on each of the points of dispute and pass a reasoned and speaking Award thereon, within the Terms and Conditions of the Contract Agreement.

(IX) If any difference remains after an Arbitral award, and an appeal could be raised under the Arbitration and Conciliation Act, 1996, the appropriate Court within the Jaipur , Rajasthan shall deal with the matter.

TECHNICAL SPECIFICATIONS – DG SETS

MAINS FAILURE STANDBY GENERATING SYSTEM (D.G. SETS)

Work Description

The specification covers Supply to site , installation ,Testing and  Commissioning

Scope of Work

The scope of work shall include design, manufacturing, pre delivery inspection,  installation  testing and commissioning of D.G. Sets and items as described below:

The work shall be executed as per Central Electrical Authority and Central Pollution control board - IV or latest norms as specified in tender specifications. DG Sets will be CPCB-IV compliant.

DG Sets are to be installed outdoor and shall be provided with acoustic enclosure as per CPCB norms.

The cooling system of DG Sets is proposed with radiator.

Diesel engine & alternator set complete with base frame and accessories.

Integrated control panel duly wired up to terminal box for engine safeties, Full Authority Electronic Fuel injection system, digital Governor, metering and protection & compatible for interfacing with PLC Engine mounted or separately mounted. Gen set Controller shall be microprocessor based.

Fuel oil system with piping, valves filters etc. from engine to service day oil tank. Return fuel line with fuel cooler and piping with accessories up to day service tank or collecting point as called for.

Lube oil system with inbuilt pump & connecting piping etc.

Exhaust emission meeting pollution norms (CPCB & SPCB) with Critical grade silencer, exhaust piping with mineral wool insulation and aluminium cladding as called for.

D.G. supplier shall furnish back up combined guarantee minimum for 12 months years from the date of successful commissioning from Engine and alternator supplier for their smooth operation. In case any defect is noticed during operation or for any other reason, the same shall be attended promptly and repair/ replacement of any component in part or in whole will be made immediately at no extra cost to the Project manager-LNMIIT.

OEM/ Manufacturer’s Instructions

Where manufacturers have furnished specific instructions, relating to the material/ equipments to be used on this job, covering points not specifically mentioned in this document, manufacturer’s instructions should be followed.

Completion Documents and Drawings

Three copies of operation manuals/ catalogues of all standard equipment are to be furnished by the Contractor immediately after commissioning of plant.

Three copies of write up on preventive maintenance, trouble shooting and operating instructions of the system along with as-built drawings are to be supplied by the Contractor at the time of commissioning.

On completion of the work in all respects, the Contractor shall supply five portfolios (300x450 mm), each containing complete set of drawings on approved scale, clearly indicating complete layouts, location; wiring and sequencing of automatic controls, location of all concealed wiring and other services. Each portfolio shall contain consolidated control diagrams and technical literature on all controls. The Contractor shall frame under glass one set of these consolidated control diagrams for display in the panel room.

Degree of Protection:

The degree of protection in the enclosures of the control cabinet, junction and marshalling boxes, panels, etc. shall be as detailed here under:

| 1. | Installed indoor | : IP-55 |
| --- | --- | --- |
| 2. | Installed indoor in air-conditioned area | : IP-31 |
| 3. | Installed in covered area | : IP-42 |
| 4. | Installed indoor in non-air-conditioned area Where possibility of entry of water is limited | : IP-41 |
| 5. | For LT Switchgear (AC and DC distribution boards) | : IP-42 |

The degree of protection shall be in accordance with IS: 13947 (Part –I) and IEC-947 (Part –I). Type test report for degree of protection test on each type of the box shall be submitted for approval of Project manager-LNMIIT.

Rating plates, Name plates and Labels:

D.G. Sets, control panel and auxiliary items installed in the building are to be permanently attached to it in conspicuous position. A rating plate of non-corrosive material with engraved manufacturer’s name, year of manufacture, equipment details type or serial number together with details of designed loading conditions of operation.

Equipment’s rating plate shall be in accordance with IEC requirement.

All such name plates, instruction plates, rating plates shall be bilingual with Hindi inscription first followed by English. Alternatively, two separate plates one with Hindi and another with English inscriptions may be provided.

First fill of consumables, Oil & Lubricants:

All the first fill of consumables such as oils, lubricants, filing compounds, touch up paints, welding/ soldering/ brazing material for all Copper/ G.I earthing and essential chemicals etc. which will be required to put the equipment/ scheme covered under scope of the specifications, into successful operation, shall be furnished by the OEM unless specifically excluded under the exclusions in the specifications/ documents.

Quality Assurance Documents:

The Contractor shall be required to submit the following Quality Assurance Documents within three weeks after dispatch of the equipment.

All Non-Destructive Examination procedures, stress relief and weld repair procedure actually used during fabrication and reports including radiography interpretation reports.

Welder and welding operator qualification certificates.

Welder’s identification list, listing welder’s and operator’s qualification procedure and welding identification symbols.

Raw material test reports on components as specified by the specification and/ or agreed to in the quality plan. Stress relief time temperature charts/oil impregnation time temperature charts.

Factory test results for testing required as per applicable codes/ mutually agreed quality plan/ standards referred in the technical specification.

The quality plan with verification of various customer inspection points (CIP) as mutually and methods used to verify the inspection and testing points in the quality plan were performed satisfactorily.

Inspection, Testing and Inspection Certificates

The Project manager-LNMIIT shall have at all reasonable times free access to the Contractor’s premises or works and shall have the power at all reasonable times to inspect and examine the materials and workmanship of the works during its manufacture or erection, if part of the works is being manufactured or assembled at other premises or works, the Contractor shall obtain permission to inspect as if the works were manufactured or assembled on the Contractor’s own premises or works. Inspection may be made after manufacturing prior to dispatch at site at the option of the Project manager-LNMIIT and the equipment if found unsatisfactory due to bad workmanship or quality, material is liable to be rejected.

DG Set factory acceptance test witness shall be offered for 2 hrs. with water load bank on unit power factor after assembly to Engineer In-Charge and following minimum tests should be offered:

No load test – 10minutes

25% Load – 10minutes

50% Load – 10minutes

75% Load – 30minutes

100% Load – 30minutes &

110% Load – 30minutes

DG SET PERFORMANCE PARAMETERS LIKE VOLTAGE, HZ, AMP., KW, PF, COOLANT TEMP., LUB.

OIL Pr. ETC. SHALL BE RECORDED DURING TRIAL.

Fuel consumption at 100% load & vibration checks also needs to be done & ensured.

All equipment being supplied shall conform to type tests and shall be subject to routine tests in accordance with requirements stipulated under respective sections. Bidder shall submit the type tests reports for approval. The Contractor shall intimate the Project manager-LNMIIT the detailed program about the tests at least three (3) weeks in advance in case of domestic supplies. If for any item type test were pending payment would be made on successful completion of type/ routine test(s) actually carried out as per Project manager-LNMIIT instructions.

The Contractor shall give the Project manager-LNMIIT thirty (30) days written notice of any material being ready for testing. Such tests shall be to the Contractor’s account. The Project manager-LNMIIT unless witnessing of the tests is virtually waived will attend such tests within thirty (30) days of the date of which the equipment is notified as being ready for test/ inspection, failing which the Contractor may proceed with the test which shall be deemed to have been made in the presence of Project manager-LNMIIT and shall forward duly certified copies of tests in triplicate.

The Project manager-LNMIIT within fifteen (15) days from the date of inspection as defined shall inform in writing to the Contractor of defects noticed during inspection and any objection to drawings or workmanship which in his opinion is not in accordance with the Contract. The Contractor shall give due consideration to such objections and make the necessary modifications accordingly.

When the factory tests have been completed at the Contractor’s or Sub-contractor’s works, the Project manager-LNMIIT shall issue a certificate to this effect within fifteen (15) days after completion of tests but if the tests are not witnessed by the Project manager-LNMIIT, the certificate shall be issued within fifteen (15) days of receipt of the Contractor’s Test certificate by the Project manager-LNMIIT. Failure of the issue such a certificate shall not prevent the Contractor from proceeding with the works. The completion of these tests or the issue of the certificate shall not bind the Project manager-LNMIIT to accept the equipment should, it, on further tests after erection, is found not to comply with the Specification.

The equipment shall be dispatched to site only after approval of test reports and issuance of MICC by the Project manager-LNMIIT.

For tests whether at the premises or at the works of the Contractor or of any Sub Contractor, the Contractor except where otherwise specified shall provide free of charge such items as labor, materials, electricity, fuel, water, stores, apparatus and instruments as may be required by Project manager-LNMIIT or this authorized representative to carry out effectively such tests of the equipment in accordance with the Specification.

The inspection by Project manager-LNMIIT and issue of Inspection Certificate thereon shall in no way limit the liabilities and responsibilities of the Contractor in respect of the agreed quality assurance program forming a part of the Contract.

Tests

Charging (Pre-commissioning tests):

On completion of erection of the equipment and before charging, each item of the equipment shall be thoroughly cleaned and then inspected jointly by the Project manager-LNMIIT and the Contractor for correctness and completeness of installation and acceptability for charging, leading to initial pre-commissioning tests at Site. The pre-commissioning tests to be performed as per relevant I.S./ manufacturer/ bidder submittal and as included in the Contractor’s quality assurance program.

Commissioning Tests:

The available instrument and control equipment will be used during such tests and the Contractor will calibrate all such measuring equipment and devices as far as practicable. However, immeasurable parameters shall be taken into account in a reasonable manner by the Contractor for the requirement of these tests. The tests will be conducted at the specified load points and as near the specified cycle condition as practicable. The Contractor will apply proper corrections in calculation, to take into account conditions which do not correspond to the specified conditions.

All instruments, tools and tackles required for the successful completion of the Commissioning Tests shall be provided by the Contractor, free of cost.

Pre-commissioning test shall be carried out as per relevant IS/ manufacturer recommendations and/or as specified in the relevant clause.

The Contractor shall be responsible for obtaining statutory clearances from the concerned authorities for commissioning of the equipment. However, the necessary fee shall be reimbursed by Project manager-LNMIIT on production of requisite documents.

Packaging:

All the equipments shall be suitably protected, coated, covered or boxed and crated to prevent damage or deterioration during transit, handling and storage at Site till the time of erection. While packing all the materials, the limitation from the point of view of availability of Railway wagon/ truck/ trailer sizes in India should be taken account of the Contractor shall be responsible for any loss or damage during transportation, handling and storage due to improper packing. Any demurrage, wharfage and other such charges claimed by the transporters, railways etc. shall be to the account of the Contractor. Project manager-LNMIIT takes no responsibility of the availability of any special packaging/ transporting arrangement.

Protection:

All coated surfaces shall be protected against abrasion, impact, discoloration and any other damages. All exposed threaded portions shall be suitably protected with either a metallic or a non-metallic protecting device. All ends of all valves and piping and conduit equipment connections shall be properly sealed with suitable devices to protect them from damage. The parts which are likely to get rusted, due to exposure to weather should also be properly treated and protected in a suitable manner.

Finishing of Metal Surfaces:

All metal surfaces shall be subjected to treatment for anti-corrosion protection. All ferrous surfaces for external use unless otherwise stated elsewhere in the specification or specifically agreed, shall be hot dip galvanized after fabrication. High tensile steel nuts and bolts and spring washers shall be electro galvanize. All steel conductors used for earthing/ grounding (above ground level) shall be galvanized according to IS: 2629.

Painting:

All sheet steel work shall be degreased and phosphated in accordance with the IS-6005 “Code of practice for Phosphate iron and sheet”. All surfaces which are not easily accessible after shop assembly, shall beforehand be treated and protected for the life of the equipment. The surfaces, which are to be finished painted after installation or require corrosion protection until installation, shall be shop painted with at least two coats of primer. Oil, grease, dirt and swab shall be thoroughly removed by emulsion cleaning. Rust and scale shall be removed by pickling with dilute acid followed by washing with running water, rinsing with slightly alkaline hot water and drying.

After Phosphating thorough rinsing shall be carried out with clean water followed by final rinsing with dilute dichromate solution and oven drying. The phosphate coating shall be sealed with application of two coats of ready mixed, stove type zinc chromate primer. The first coat may be “flashing dried” while the second coat shall be stove.

Powder coating/ electrostatic painting of approved shade shall be applied.

The exterior color of the paint shall be as per IS-5 or as approved by Project manager-LNMIIT. A small quantity of finishing paint shall be supplied for minor touching up required at site after installation of the equipments, if required.

In case the Bidder proposes to follow his own standard surface finish and protection procedures or any other established painting procedures like electrostatic painting etc. the procedure shall be submitted along with the Bid for Project manager-LNMIIT attention and consideration.

Diesel Engine – Construction

Material of construction of major parts shall be as under or as per manufacturer’s standard design.

M.S. base frame with anti-vibration mountings.

Crankcase – Aluminium alloys.

Crank shaft, connecting rods – Forged Alloy Steel.

Piston – Al. alloy casting

Piston rings – Alloy steel

Engine block – Cast iron.

Cylinder liner – Cast

All other materials of construction shall be as per relevant standard/ code and the copies of same shall be supplied free of cost to Project manager-LNMIIT.

The Diesel Engine shall be multi-cylinder, 4-stroke, water cooled with engine mounted radiator, totally enclosed, continuous duty, direct fuel injection, turbo charged, compression ignition, inter cooled oil engine or with individual cylinder head with provision to measure exhaust temperature.

One common base frame shall be provided for mounting the engine and alternator complete with AVM pads between DG set and foundation, leveling lines etc. as required.

All externally mounted hardware shall be high tensile steel only.

The engine shall be fitted with an exhaust gas driven turbo charger of air/ water cooled type complete with its own self-contained lubricating system. The turbocharger shall be positioned at the free end of the engine preferably.

The engine shall be fitted with a charge air inter cooled of the air/water type. Air from the turbo-charged compressor passes through the inter cooler and then to the engine manifold. The inter cooler shall be of tubular construction or as per manufacturer design with aluminium bronze tubes, mild sheet steel and cast-iron water headers.

Contractor shall indicate the maximum time for which the Diesel Engine can be operated.

Governing System

The Governor shall be electronic fuel control type for coupled Generating set with over speed trip protection.

Engine Starting System

Starting of the Diesel Engine shall be done by electric starting system.

The electric starting system shall comprise starter motor, batteries (4nos. 12V 160AH capacity OR as per manufacturer’s recommendation suitable for 3consucutive starts) and battery charger including with all required instruments and accessories.

The engine mounted charging alternator shall charge the batteries while engine is running, and Panel/ floor panel mounted solid state battery charger while engine is stationery. The battery charger shall be rated for boost and trickle charge with all metering and control instruments and protections for A/C and D/C circuit. The total system shall be suitable for auto and manual operation including their wiring etc. Calculation for the battery and battery charger capacity as well as complete descriptive circuit diagram based on three consecutive start commands shall be submitted for approval of Project manager-LNMIIT.

Fuel Oil System

The manufacturer shall furnish a mild steel day tank of required capacity for individual engine. The day tank shall be suitably located to avoid gravity feed to the engine, shaft driven fuel oil pumps and shall be complete with gauges, filling, draining and vent connection with valves and level switch for auto filling of tank and for alarm in case oil level goes beyond specified limit.

The fuel system shall be provided with full flow simplex oil cartridge filter.

The fuel oil system shall be equipped with a crankshaft driven fuel oil transfer pump which will draw the fuel oil from the day tank via filters and shall be as per the engine manufacturer design.

Multi point (electronically controlled) fuel injection system or direct injection/ through is ochronous fuel Governing system shall be designed taking into account the type of fuel used, engine speed etc. so as to achieve safe knock free performance with low emission smoke.

Lubricating Oil System

All lubricating parts of the engine shall be connected to a pressurized lubricating oil distribution piping system being continuously charged by gear type lube oil pump mounted at the free end of the engine and driven from the engine crank shaft. The pumps shall take suction from a sump tank integral with the engine through a foot valve, suction filter through oil cooler and deliver oil to main supply header. High-pressure oil shall be supplied to the main and big end bearings, crankshaft bearings, governor, auxiliary drive gear etc. Suitable lubricating arrangement for engine cylinder valve gear, cams and pistons at the required level shall be arranged. A pressure relief valve shall be mounted on the main supply header for safety against too high-pressure while starting with cold oil. A timer based, auto running (auto priming pump) shall be provided to keep engine primed all the time complete with control system (if required).

The lube oil system shall be provided with full flow simplex lube oil cartridge filters. The minimum lube oil change shall be after 300 hrs. of operation.

Arrangement shall be provided to bypass the lube oil pressure switches and safety at the starting till the pressure is built up.

The lube oil sump shall be provided to sense the low level of lube oil in the sump and fill it up automatically from the main lube oil tank/ sump and stop the transfer pump, once the lube oil is filled in the sump without stopping the engine. Pressure switches to give alarm under extreme low pressure of lube oil and subsequently to trip the unit, when the minimum safe pressure has reached, shall be provided.

All necessary accessories such as pressure gauges, temperature indicators, pressure relief valves, bypass valves, pressure switches shall be provided, and the safeties shall be wired up to junction box

Exhaust System

Engine emission exhaust silencer shall be critical type Silencer to ensure minimum 25 dba insertion loss as per CPCB, ducting, bends, hood/ canopy, thermally insulated 75mm thick compressed mineral LBR (Rock wool) having 150Kg/m3 density for D.G. exhaust pipe with 22-gauge aluminium sheet cladding etc. shall be provided along with structural support with stays for each engine. Heat resistant paint shall be provided on exhaust pipe for the portion, which is outside of the building/ stack uninsulated. Exhaust system pollution level shall be indicated and got approved by authorities. (Exhaust smoke quality & quantity should be within the norms of central & state pollution control board).

Emission standards in brief for above 800KW (at 0.8pf) Engines – Generator set application

NOx (up to 75MW) – 710 ppmv

HC – 100 ppmv

PM – 75 mg/ Nm3

CO – 150 mg/ Nm3

Sulphur contains in fuel - <2%

Engine Alternator Control Panel

Engine alternator (D.G.) controller panel shall be provided with digital display for speedometer, lubricating oil pressure gauge, jacket water temp, battery charging, for local indication & panel mounted on/ near the engine itself.

Engine shall be supplied with microprocessor based Genset Controller for diesel generating set monitoring control system, which should be equipped with (digital) electronic Governor along with digital AVR to facilitate discreet control of speed and voltage in synchronous mode.

The system shall be equipped with starting control including integrated fuel ramping to limit the black smoke frequency overshoot with optimized cold weather starting. The engine instrument panel shall be equipped with digital alarm and status to monitor and display the following parameters. The interface modules, converter, probe and their wiring up to terminal block in panel with 485 ports etc. making compatibility with PLC. The necessary CT/ PT shall be included and wired accordingly to meet the requirements.

Engine Indicators:

Digital tachometer with running hour meter

Lubricating oil pressure low

Over speed

Engine fail to start

Lack of fuel due to low level.

Volts RY-YB-BR.

Amps R-Y-B.

AMF Control Panels

Control Philosophy:

Automatic Starting and Stopping of Engines:

The system should come in operation after sensing of Grid Failure and/ or the voltage drops below preset value. For this purpose, the NB-2 or equivalent “Engine Control & Automatic Mains Failure Stand by System” shall be provided to perform the following functions.

Sensing the healthiness of supply from Supply Company, the engine shall be at rest.

On sensing the supply healthiness (the supply fails or drop below the preset value) the command shall be given to start the D.G. Set.

In case the D.G. Set does not start in the 1st command than two more commands shall be given to start the D.G. Set at an equal interval of time (5 Sec). Even if the engine does not start the indication shall appear on window/ screen “Set fail to start” and alarm shall be generated. On starting of D.G. Set & monitoring the healthiness of supply, the load shall automatically be transferred on D.G.

On restoration of the supply & monitoring the healthiness of the system, the load shall be transferred to Mains automatically & vice versa.

Manual Mode:

Select manual mode on the relay unit.

The Set shall only be started by pushing the “start button” on the relay.

On attaining the requisite voltage & frequency, the D.G. breaker/ Contactor will be closed or tripped manually without shutting down the engine.

The Engine shall be shut down manually by pressing the push button.

Test Mode:

The test mode operation is independent of the conditions of the mains supply & thereby enables routine testing or exercising of the D.G. Set without closing the D.G. breaker/ contactor. (Select the switch on selector mode & is similar to the auto mode except closing of the breaker).

The relay shall have following features such as:

Mode selector switch (Auto/ Manual/ Test/ Off)

Engine Control switch (On/ Off push button)

Reset/ Acknowledge push button.

Breaker close/ open push button.

Test push button.

Set of visual indication

Load on Mains.

Load on D.G. Set.

Set fails to start.

Low-pressure alarm & Trip.

High temperature alarm & Trip.

Engine over speed.

Alternator overload & short circuit.

Voltages, phase to phase & phase to neutral.

Ammeter Line/ Phase current.

Power factor meter.

Kilowatt-hour meter.

Frequency meter.

Tachometer.

Alternator (415V – 3 Phase, 4 Wire System)

The alternator shall be brushless synchronous and suitable for 3 phase 415V, 4 wire, 50 Hz, 0.8 p.f., 1500 RPM.

The alternator shall be suitable for coupling directly to the diesel engines described earlier in clause no. 1.0 It shall be Drip proof, screen protected as per IP-23. It shall include one set of suitable rated foot mounted anti - condensation heaters. The alternator shall be single/ double bearing type and self-ventilating. The Alternators shall be provided with fully interconnected damper windings to facilitate parallel running. The alternators shall be continuously rated and shall have class 'F' insulation designed and built to withstand tropical conditions. It shall generally conform to BS: 5000 (part - 99). The rated output of alternators at specified site condition at 0.8 lagging power factor shall be 1600kW for 1500kVA DG Set at 415V. Each DG set shall be suitable for sustaining a 10% overload for 1 hour in any 12-hour period without injury. Additional adopter box to be provided for accommodating outgoing Al. Conductor cables including G.I. nut bolts for termination.

The alternator shall also have a digital automatic voltage regulator (AVR inbuilt in Genset Controller) suitable for single and parallel running with control limits of 1% from no load to full load under normal load changes when running single.

The Engine and Alternator shall be direct coupled and mounted on a common rigid fabricated steel base frame with suitable vibration isolation system.

The Alternator shall withstand an over speed of 20% for a period of 2 minutes without mechanical damage.

The generator/ alternator shall with stand overload of 10% for 1 hour every 12 hourly. The terminal voltage shall be adjustable, and the range of adjustment shall be +/- 5% of nominal voltage.

The Alternator shall be capable of withstanding 3-phase short circuit at its terminals for 3 seconds when operated at rated kVA and power factor at 5% over voltage with fixed excitation (3 times the line current for 10 Sec) without damage/ injury.

The alternator shall be capable of withstanding 50 % excess of rated current for 30 seconds at maintained rated voltage, consistent with max capacity of the prime mover.

Six Nos. embedded (RTD) resistant temperature detector platinum (100-ohm resistance at 0 Degree) to measure the winding temperature and 1/2 Nos. (BTDS) bearing temperature detector shall be provided.

The leads of embedded RTD shall be wired up to the terminal block in a separate auxiliary terminal box.

Manufacturer shall indicate the setting values for each RTD/ BTD for alarm and trip.

All external nuts and bolts shall be of high tensile steel only.

Alternator shall be provided with anti-condensation space heater of adequate rating suitable for 240V, 50 Hz. single ph A.C. supply and shall be wired up to a separate terminal box. (Wiring and equipment shall be provided by D.G. supplier).

Two independent earth terminals on the frame complete with nuts, spring washer and plain washer shall be provided.

Alternator shall be provided with suitable terminal box for terminating cables drop and protection. CTS within the terminal box duly wired up to the panel shall be provided.

The alternator shall be capable to sustain the unbalanced current between the phases minimum 25% of rated current provide that the kVA rating.

The alternator shall be fitted with radio interference suppressors in accordance with BS-613-1977 and shall be within the limit of CISPR standard.

The alternator shall be dynamically balanced complete with rotor and shaft.

Alternator should have bearings at one/ both shaft ends.

Damper winding shall be provided in the pole to damp the oscillations and ensure satisfactory performance during parallel operation.

Winding of 3 phase alternators shall be of star connected and neutral point shall be brought out to the terminal box through protection and earthed with independent earth or through contactor as per scheme. Protection CT’s/ PT’s shall be mounted above the terminal box with enclosure. Bus duct/ cable shall be terminated on terminals through this.

Diesel generating set shall be able to start motor of 30% capacity of D.G. set with a 20% base load.

Automatic Voltage Regulator

An automatic/ digital high speed voltage regulator (inbuilt in genset controller) shall be provided with all accessories. The regulation system shall be with equipment accessories for automatic control.

The combined voltage regulation shall be ± 1% from full load to no-load, from hot to cold at 0.8 power factor with 4% speed regulation of the engine.

Necessary equipment for field suppression and surge protection shall be provided.

The response time of the exciter and the generator shall be matched to avoid hunting.

Reactive load sharing of parallel operating generator shall be in proposition to their ratings. The quartrative drop current transfer compensation feature should be provided on exciter regulation and drop voltage shall be within 1% variation.

D.G. Set Vendor shall inspect the existing system and include all necessary hardware, input/ output modules and junction box with terminal block and its wiring complete as required to make the system operational in PLC/ Manual mode and to be included in price bid.

PLC System

Note:

D.G. Vendor shall include all necessary hardware, input/output modules and junction box with terminal block complete as required to make the system operational in PLC/ Manual mode and to be included in price bid.

Control Philosophy (Only for Information)

Automatic Starting & Stopping of Engines:

The system should come in operation after sensing of grid failure or the voltage drops below preset values. The 'PLC' shall issue the command to 'Master' D.G. set. In case the D.G. set fails to start in the 1st cranking, two more cranking attempts shall be made with proper intervals. Even then if engine fails to start, indication must appear on MMI/ Monitor 'Set Fails to Start' & alarm shall be generated. The PLC shall give the command to the next DG set selected in sequence.

DG set on load operation system shall start monitoring voltage, frequency and load. If the load exceeds settable limit the next D.G. shall be started to prevent D.G. over loading. The process shall continue till all the D.G. sets have been started.

At any point of time the engines are under loaded and the load is capable of being catered by less than the numbers of running DG sets. Stop command shall be given to DG running for shortest duration at that moment.

On restoration of mains and sensing the healthiness of the same, the load shall be transferred to mains. The DG sets shall be given stop command after settable time delay ensuring adequate cooling down of the engine.

Auto Synchronization:

Synchronization facility shall be available both for ‘Auto & manual’ mode. an auto mode, the synchronization will be achieved by 'PLC' (PLC will control voltage, frequency and phase angle and issue command to breaker), However if due to any reason auto synchronization fails repeatedly the ‘PLC' system should initiate start command to next DG for operation as well as synchronize the system automatically.

In manual mode the system shall be manually operated backed by relays.

In auto mode facility the closing of breaker shall be automatic, whereas in manual mode breaker will be closed by panel switch through synchronizing relay.

In any case if the auto synchronization is failed to achieve in a settable time an alarm shall be generated and displayed that the 'DG Failed to Synchronize' and the same shall be aborted.

Automatic Load Sharing:

'PLC' shall monitor active & reactive power generated by the various sets continuously and shall issue command to achieve proper load sharing.

Back up Protection:

The system shall have built-in protection as listed below and shall continuously monitor the parameters and on sensing of any electrical fault PLC shall trigger 'Trip command’. Through Trip relay of the corresponding breaker similarly in case of semi auto mode and in case of manual mode it shall be through master trip relay.

Over voltage/ Under voltage

Over frequency/ Under frequency

Over Current

Reverse power active

Active Power reactive

Synchronizing check (MMI)

Earth fault relay unbalance

Differential protection through relay interface with PLC/ PC

Engine Protection as listed under DG sub-head shall also be interfaced with PC/ PLC for generating trip command/ alarm and generating report etc.

Programmable Logic Controller (PLC):

The entire operation of the captive power generation system and grid supply shall be controlled automatically through PLC. These PLC’s shall be state-of-the-art equipment using latest technology and of most rugged and reliable design. Since system will be operating in the harsh and unfriendly environment of D.G. Room, they should be suitable to operate trouble free under the conditions. The selected equipments should be able to withstand high temperature, humidity and voltage fluctuations, thus making it suitable for the operating conditions described above.

Automatic PLC system basically shall consist of but not limited to:

Main processor unit

EEPROM for CPU Power supply unit I kVA UPS with maintenance free batteries for 30-minute Capacity

Mounting chassis 16/ slot mounting rack

Line Synchronization module

Digital input module

Digital output module

Computer to PLC communication card with cable (MMI)

Operator interface graphics software package (Windows based)

Analog I/ P & O/ P module 16/ 8 channels

Outgoing circuit (KWH) meter with pulse counter interface with PLC for generating report 20% spare incoming/ outgoing shall be provided for future use. Interfaced connectivity for engine safeties and meters with cabling etc.

System diagnostic card control for DG auxiliary (Pump, fans, oil, fuel, cooler. etc.) Monitoring of HT voltage Transformer’s alarm and trip mimic of 33kV & LV system

Monitoring of electrical parameters, incoming and outgoing Circuit Breaker of high and low voltage circuit and PC complete with CPU, colored monitor, keyboard, laser printer, required software shall be installed and commissioned.

Sequence of Operation for Auto Start-Stop, Auto Synchronizing, Auto Load Sharing and Load Management of D.G. Sets:

‘On Grid’ Supply failure or on sensing of grid supply voltage (voltage drop than preset value), the master DG shall start automatically and closes its breaker/ neutral contactor. Bus breaker also closes to feed the loads.

On attainment of maximum permissible load on master DG set (I). The 2nd shall start automatically.

Auto Synchronizing system shall verify the phase angle and also compensate closing time of incoming breaker by initiating closing command to breaker ahead of the actual on predictable Synchronizing ensuring thereby a zero (0) degree phase difference, as well as the system shall monitor the slip frequency, beat (hunting) voltage of the machine or system.

First DG neutral contactor shall remain in circuit even if the 1st DG set is shut-off. The neutral contactor of the other working set shall get closed first before tripping of the shutting off DG Set.

The process shall continue for incoming DG's such as 3rd, 4th so on.

The starting sequence of the DG sets can be altered through (MMI/ PLC).

ON restoration of grid supply and sensing of healthiness of the same. The DG's & bus breaker shall be ‘out' and grid breaker shall be ‘in' to feed the power. Active power on DG's is balanced automatically through Governor Control with the help of Active Load Balancing System.

Reactive load balancing system to achieve kVAR and regulation within preset bank value through the motorized potentiometers.

In the event set fails to synchronize the alarm generated through Annunciation panel shall invite the attention of the Operator for 'Manual' intervention. If the sets do not synchronize the bus breakers shall be switched off and both the sets start feeding their respective loads.

In the event of a D.G. standing idle more than 8 hours lube oil priming pump shall be started for 3-5 minutes.

DG auxiliary feeders shall be controlled through 'PLC' for starting/ stopping of respective DG auxiliary system.

The system shall have total manual over-side w/o (without) by-passing the safeties and protections.

The system shall facilitate program changeability/ settings/ time delay etc. through MMI on PC.

Stand Alone Mode (No Synchronizing):

In this case the system shall work independently with electrical inter-linking to prevent parallel operation of two supply sources.

Function/ Feature of PLC System:

In general terms the following will be the functions of PLC. During final freezing of the controls, logic & Dos, addition and deletions can be made through PLC (MMI)

The system shall directly accept CT & PT signals without need of any transmitters for electrical parameter monitoring and control system or the same shall be met through energy monitoring/ management relays with RS 485 communication port.

Starting and stopping of DG sets automatically with by-pass arrangement in PLC depending upon the load requirement.

Automatic selection of next DG as master after stopping/ tripping of master DG & to close or open of neutral contactor respectively.

Automatic Synchronizing of DG sets in auto mode.

The system shall run on manual mode with relay protection back up in the event of PLC failure.

Key for selection of number of DG sets to start and synchronize at no load for kick (starting) load requirements.

Active & reactive power sharing of each DG sets.

Monitoring of electrical parameter on each D.G., voltage, frequency, reactive load, active load, and energy produced etc.

Status and control of outgoing breakers.

Backup protection electrical by time delayed tripping of DG set.

Alarm and trip for reverse power, reverse kVAR, under voltage, over voltage, under frequency, over frequency, over current, low lube oil pressure, over speed and other safeties as called for in DG tender.

Data acquisition system will be incorporated with the system for the purpose of recording. The maintenance of the system and in totality operation system l important and critical parameters of the engine, alternator will be through operator interface and displayed with graphic screen.

PLC system should be capable to take care of all the protection (relay features) in auto mode. Relay base protection features of manual mode shall also be compatible with PC.

'B' checks alarm after each DG complete 500 hours or as recommended by DG supplier of running for proper maintenance.

Tripping of less priority loads in the building in case of under frequency of bus both in isolation as well as synchronized mode.

PLC input/ output cards should be dedicated to individual DG’S without intermingling of signals from different DG’S.

PLC system shall have provision to test the DG in auto mode without closing the breaker to do the routine electrical/ mechanical test without interruption of power generation.

Monitoring of 6 points alternator winding, 2 points bearing temp drive and non-drive, ends for alarm & trip respectively. Provision for monitoring of 2 points exhaust gas temperature and smoke quality.

Besides DG’S PLC will also monitor grid supply parameter such kW, kWH, kVA, kVAR, as well as of the outgoing feeders etc. these parameters shall also be available to connect to BMS system as well.

The following minimum points but not the list, to be taken care by DG manufacturer and need to provide informations/ details as per below details for BMS purpose.

| Sr. No. | Description | Qty | AI | DI | AO | DO | S.I. | By IBMS Provider | By respective 3rd party contractors |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| i) | Diesel Generator | 2 |  |  |  |  |  |  |  |
| 1 | DG Run Status |  |  | 2 |  |  |  | Wiring & termination | Termination details of potential free contact in RUN mode in the control circuit |
| 2 | DG Battery Voltage Status |  | 2 |  |  |  |  | DC Voltage Transducer (0-30V DC transducer) | Suitably space for installation of Voltage Transducer |
| 3 | DG Individual Day Oil Tank Status |  | 2 |  |  |  |  | Flameproof level transmitter for day tank | Suitable flange to be provided by DG Vendor for mounting level transmitter |
| 4 | DG Microprocessor (Software Integration for DG) |  |  |  |  |  | 40 | Transfer Parameter for to BMS from DG over Serial Communication on BACnet/ MSTP or on MODBUS-RTU | DG Vendor to confirm the Points to be released to BMS Vendor & communication protocol on Modbus/ RS485 or BACnet |

The system supplier shall include the cost of the 1 spare card for each system to facilitate maintenance.

The system supplier will supply 6 sets of as built drawings along with trouble shooting with suggested measurer operational and maintenance guidelines through Project manager-LNMIITs.

Manual Mode

In this case complete system operation will be done manually. Hence the starting of the DG sets, synchronization procedure, breaker closing, tripping etc. will be done through respective switches, push buttons provided on respective feeders.

In this mode load sharing units will be effective hence starting or stopping of DG sets is done manually only.

Note: Any hardware/ software required to make the system operational in PLC/ manual mode shall be provided by the contractor.

Neutral Closing System for Parallel Running of DG set

A suitably rating L.V. contactor shall be provided for each DG set for neutral isolation controlled through PLC (auto/ manual) from remote. The neutral contactor of the DG set started first will be closed and then command for that ACB closing can be effective. Only one neutral contactor (of the first DG set) will be closed during parallel operation.

In event of tripping of neutral contactor for master D.G. set the next selected DG’S N.C should close before the N.C of the master DG trip. While switching ‘OFF” the DG sets which have started first is selected then the neutral contactor of either of remaining set will be switched on and then tripping signal to the first started D.G set will be actuated.

After voltage and frequency reached the set band, PLC shall issue close command to N.C 1st and then to ACB of selected DG set. This will prevent fault level current from flowing into the system. At any moment of time only neutral is the system to avoid any circulation current in other alternator.

The operational mimic shall also be provided for complete function of mains & DGs etc. on the box.

Commissioning Checks

In addition to the checks and test recommended by the manufacturer, the Contractor shall supervise the following commissioning checks to be carried out at site.

Load Test (at site):

The engine shall give test run for a period of at least 6 hours. All instruments, materials, consumables (fuel oil, lub. Oil etc.) load and labour required for carrying out of the test at site shall be arranged by contractor. The set shall be tested as per instructions by Project manager-LNMIIT without exceeding the specified D.G. Set rating:

During the load test, half hourly records of the following shall be taken:

Ambient temperature

Lubricating oil temperature

Lubricating oil pressure.

Color of exhaust gas.

Speed.

Voltage, wattage and current output.

Oil tank level.

Insulation Resistance Test for Alternator:

Insulation resistance in mega-ohms between the coils and the frame of the alternator when tested with a 1000V megger shall not be less than.

IR = 2 x (rated voltage in kV) + 1

Fuel consumption Check:

A check of the fuel consumption shall be made during the load run test. This test shall be conducted for the purpose of proper tuning of the engine.

Insulation Resistance of Wiring:

Insulation resistance of control panel wiring shall be checked by 500V megger. The IR shall not be less than one mega ohm.

Functional Tests:

Functional tests on control panel.

Functional test on starting provision on the engine.

Functional tests on all Field devices.

Functional tests on AVR and speed governor (visual).

Vibration Measurement:

The vibration shall be measured at Load as close to maximum achievable load and shall not exceed 130 microns/ ISO 8528 limits.

Noise Level Measurement:

DG Room Noise level shall be measured as per ISO 8528, noise level should be within limits of CPCB/ MOEF guidelines.

Test Certificates and Reports:

Test Certificate shall be submitted in four (4) copies.

The test certificates shall be furnished to the Project manager-LNMIIT for prior approval before dispatch of any equipment from works and the approval in writing from Project manager-LNMIIT shall be essential to effect dispatch of the equipment.

The test reports shall furnish complete data for equipment identification.

| LIST OF APPROVED MAKES FOR DG SET SUPPLY WORKS |  |  |
| --- | --- | --- |
| S.No. | Description | Makes |
| 1 | DG Set- Engine | Baudouin/ Cummins/ Greaves |
| 2 | DG Set- Alternator | AVK-SEG/ Leroy Somer/ Stamford/ Crompton & Greaves |
| 3 | DG Controller | Cummins/ Dieff/ Deep Sea/ Wood Word/ Greaves |

In case any of makes for any of the material is missed out in the above list for using at site then the contractor shall inform the Project Manager-LNMIIT about the same and obtain the approval. Thereafter, he can proceed with the supply of the material.

SCHEDULE OF QUANTITIES

| SL. NO. | ITEM DESCRIPTIONS | UNIT | QTY. |
| --- | --- | --- | --- |
|  | DG SET WORKS |  |  |
|  | Design, supply, ,installation, testing & commissioning) of this DG Sets and its ancillaries: |  |  |
| 1 | SUPPLY OF D.G. SETS |  |  |
| 1.1 | DG SET WITH RADIATOR - IN ACCOUSTIC HOOD |  |  |
|  | Design, Manufacture, Supply at site of Prime Duty continuous rated 4 stroke, 750 kVA DG Set comprising of Engine of 1500 rpm, Radiator Cooled, coupled and aligned with continuous rated 750 kVA, 415V ± 1%, 3 phase, 4 wire, 50 Hz. 1500 rpm, 0.8 PF industrial type brushless, AC Alternator with electronic AVR mounted on a common base frame. Alternator shall be complete with suitable terminal box with Aluminium link work to accomodate the Aluminium Armoured cables as may be required. |  |  |
| Note: |  |  |  |
|  | Generators from 1500kVA to 3000kVA to have link work & necessary provisions to accommodate 1 No. Class 5P10 CT for standby earth fault relay. (DG set supplier not to include these CT's & Relay, but to include only necessary link work etc. at the alternator level). |  |  |
|  | Alternator shall be rated to deliver full rated capacity upto 50°C ambient temp. & upto an altitude of 1000 M above MSL. |  |  |
|  | The work shall be executed as per Central Electrical Authority and Central Pollution control board - IV or latest norms as specified in tender specifications. |  |  |
|  | DG Set shall be complete with following accessories: |  |  |
| a. | 3mm thick MS painted 990 litres Day Oil Tank with float & board level indicator |  |  |
| b. | Fully charged Lead Acid batteries with painted angle iron stand |  |  |
| c. | Battery leads |  |  |
| d. | Residential Silencer & Flexible coupling/ Bellows |  |  |
| e. | Base frame with Anti vibration mountings as required. |  |  |
|  | O/M Manuals, Test Certificates & Warranty certificates : |  |  |
|  | DG Set shall have 1 set (Original) + 3 sets photocopies of engine & alternator O/M manuals, Test certificates of Engine & alternator, warranty certificates of engine, Alternator & Batteries etc. |  |  |
|  | Winding RTD & Bearing RTD for alternator : |  |  |
|  | DG Sets of 1000kVA & above shall also have winding RTD & Bearing RTD for alternator & its control wiring upto the DG Power Panel. |  |  |
|  | Fuel Pump & Governor : |  |  |
|  | Engine fuel pump shall be with electrically operated actuator/ electronic/ digital governor. (From 180kVA to 3000kVA) suitable for synchronization. (To be suitable for synchronization) |  |  |
|  | Alternator AVR: |  |  |
|  | Alternators From 140kVA to 3000kVA shall be suitable for synchronization i.e. AVR with droop facility. |  |  |
|  | DG Set Controller: |  |  |
|  | The DG Set shall be complete with DG Controller. The controller shall be able to perform the following functions & monitor various parameters: |  |  |
| a. | Perform following functions: |  |  |
| i. | Manual Start/ Stop facility of DG Set through key/ Push button&with remote input acceptance for remote start and with cranking relay. |  |  |
| ii. | AMF (Auto start/ stop of DG set on normal power failure & its restoration respectively) |  |  |
| iii. | Auto synchronization of DG Sets. |  |  |
| iv. | Auto load sharing among DG Sets. |  |  |
| v. | Reverse Power Protection (Active & Reactive). |  |  |
| vi. | Auto operation (closing & opening) of DG sets breakers. |  |  |
| b. | Engine monitoring & protection: |  |  |
| i. | Lub oil pressure |  |  |
| ii. | Coolant temperature (Ambient temperature must be considered minimum 50 deg C.) |  |  |
| iii. | Engine Speed |  |  |
| iv. | Run Hour |  |  |
| v. | Battery Voltage |  |  |
| vi. | Low Lub oil pressure & warning |  |  |
| vii. | High coolant temp. warning & shut down |  |  |
| viii. | Low coolant level shut down |  |  |
| ix. | Over speed shut down |  |  |
| x. | Charging failure indication |  |  |
| xi. | Low/ high battery voltage warning |  |  |
| xii. | Fail to Crank/ Fail to start/ Shut down |  |  |
| c. | Alternator (AC) metering & protection: |  |  |
| i. | 3 Phase Amps |  |  |
| ii. | 3 Phase voltage |  |  |
| iii. | kW |  |  |
| iv. | kVA |  |  |
| v. | PF |  |  |
| vi. | HZ |  |  |
| vii. | Over voltage shut down |  |  |
| viii. | Under voltage shut down |  |  |
| ix. | Over frequency shut down |  |  |
| x. | Under frequency shut down |  |  |
| xi. | Over current shut down |  |  |
| xii. | Field overload shutdown |  |  |
| xiii. | Loss of sensing voltage shutdown |  |  |
| xiv. | Inbuilt Stop button |  |  |
| d. | Controller shall have communication port RS 485 & MODBUS TCP/ IP communication. |  |  |
| Note: | Accoustic enclosure to maintain Noise Level as per Latest CPCB norms. |  |  |
|  | DG Set with Radiator - In Accoustic hood as described above | Set | 1 |
| 1.2 | DG SET WITH RADIATOR - IN ACCOUSTIC HOOD |  |  |
|  | Design, Manufacture, Supply at site of Prime Duty continuous rated 4 stroke, 625 kVA DG Set comprising of Engine of 1500 rpm, Radiator Cooled, coupled and aligned with continuous rated 625 kVA, 415V ± 1%, 3 phase, 4 wire, 50 Hz. 1500 rpm, 0.8 PF industrial type brushless, AC Alternator with electronic AVR mounted on a common base frame. Alternator shall be complete with suitable terminal box with Aluminium link work to accomodate the Aluminium Armoured cables as may be required. |  |  |
| Note: |  |  |  |
|  | Generators from 1500kVA to 3000kVA to have link work & necessary provisions to accommodate 1 No. Class 5P10 CT for standby earth fault relay. (DG set supplier not to include these CT's & Relay, but to include only necessary link work etc. at the alternator level). |  |  |
|  | Alternator shall be rated to deliver full rated capacity upto 50°C ambient temp. & upto an altitude of 1000 M above MSL. |  |  |
|  | The work shall be executed as per Central Electrical Authority and Central Pollution control board - IV or latest norms as specified in tender specifications. |  |  |
|  | DG Set shall be complete with following accessories: |  |  |
| a. | 3mm thick MS painted 990 litres Day Oil Tank with float & board level indicator |  |  |
| b. | Fully charged Lead Acid batteries with painted angle iron stand |  |  |
| c. | Battery leads |  |  |
| d. | Residential Silencer & Flexible coupling/ Bellows |  |  |
| e. | Base frame with Anti vibration mountings as required. |  |  |
|  | O/M Manuals, Test Certificates & Warranty certificates : |  |  |
|  | DG Set shall have 1 set (Original) + 3 sets photocopies of engine & alternator O/M manuals, Test certificates of Engine & alternator, warranty certificates of engine, Alternator & Batteries etc. |  |  |
|  | Winding RTD & Bearing RTD for alternator : |  |  |
|  | DG Sets of 1000kVA & above shall also have winding RTD & Bearing RTD for alternator & its control wiring upto the DG Power Panel. |  |  |
|  | Fuel Pump & Governor : |  |  |
|  | Engine fuel pump shall be with electrically operated actuator/ electronic/ digital governor. (From 180kVA to 3000kVA) suitable for synchronization. (To be suitable for synchronization) |  |  |
|  | Alternator AVR: |  |  |
|  | Alternators From 140kVA to 3000kVA shall be suitable for synchronization i.e. AVR with droop facility. |  |  |
|  | DG Set Controller: |  |  |
|  | The DG Set shall be complete with DG Controller. The controller shall be able to perform the following functions & monitor various parameters: |  |  |
| a. | Perform following functions: |  |  |
| i. | Manual Start/ Stop facility of DG Set through key/ Push button&with remote input acceptance for remote start and with cranking relay. |  |  |
| ii. | AMF (Auto start/ stop of DG set on normal power failure & its restoration respectively) |  |  |
| iii. | Auto synchronization of DG Sets. |  |  |
| iv. | Auto load sharing among DG Sets. |  |  |
| v. | Reverse Power Protection (Active & Reactive). |  |  |
| vi. | Auto operation (closing & opening) of DG sets breakers. |  |  |
| b. | Engine monitoring & protection: |  |  |
| i. | Lub oil pressure |  |  |
| ii. | Coolant temperature (Ambient temperature must be considered minimum 50 deg C.) |  |  |
| iii. | Engine Speed |  |  |
| iv. | Run Hour |  |  |
| v. | Battery Voltage |  |  |
| vi. | Low Lub oil pressure & warning |  |  |
| vii. | High coolant temp. warning & shut down |  |  |
| viii. | Low coolant level shut down |  |  |
| ix. | Over speed shut down |  |  |
| x. | Charging failure indication |  |  |
| xi. | Low/ high battery voltage warning |  |  |
| xii. | Fail to Crank/ Fail to start/ Shut down |  |  |
| c. | Alternator (AC) metering & protection: |  |  |
| i. | 3 Phase Amps |  |  |
| ii. | 3 Phase voltage |  |  |
| iii. | kW |  |  |
| iv. | kVA |  |  |
| v. | PF |  |  |
| vi. | HZ |  |  |
| vii. | Over voltage shut down |  |  |
| viii. | Under voltage shut down |  |  |
| ix. | Over frequency shut down |  |  |
| x. | Under frequency shut down |  |  |
| xi. | Over current shut down |  |  |
| xii. | Field overload shutdown |  |  |
| xiii. | Loss of sensing voltage shutdown |  |  |
| xiv. | Inbuilt Stop button |  |  |
| d. | Controller shall have communication port RS 485 & MODBUS TCP/ IP communication. |  |  |
| Note: | Accoustic enclosure to maintain Noise Level as per Latest CPCB norms. |  |  |
|  | DG Set with Radiator - In Accoustic hood as described above | Set | 1 |
|  | Important Notes: |  |  |
| i) | All DG Sets less than 1010kVA in the indoor installation has to be with accoustic hoods. |  |  |
| ii) | All DG Sets in the out door installation irrespective of capacity has to be with acoustic hoods. |  |  |
| iii) | Vendor/ supplier to check and ensure with the Owner/ PMC on the type of DG set i.e. with or without hood before quoting and supply, irrespective of what is mentioned in this BOQ/ Specifications. |  |  |
| iv) | Vendor/ supplier to check and ensure with the Owner/ PMC on the type of DG set i.e. with heat exchanger or with radiator or with remote fluid cooler before quoting and supply, irrespective of what is mentioned in this BOQ/ Specifications. |  |  |
| v) | Vendor/ supplier to ensure suitability of the set from all aspects including need of the acoustic hood, type of the DG set like with heat exchanger or with radiator or with remote fluid cooler before quoting and supply, irrespective of what is mentioned in this BOQ/ Specifications. |  |  |
| vi) | Vendor/ supplier to check, verify and confirm to Owner/ PMC the size of the exhaust pipe for the DG sets as per site requirement based on back-pressure calculations before quoting and supply, irrespective of what is mentioned in this BOQ/ Specifications. |  |  |
| vii) | Vendor/ supplier to check, verify and confirm to Owner/ PMC the size of the cooling tower, pumps and piping for the DG sets as per site requirement before quoting and supply, irrespective of what is mentioned in this BOQ/ Specifications. |  |  |
| viii) | Vendor/ supplier to check, verify and confirm to Owner/ PMC the ventilation requirement being provided for the DG Set area. |  |  |
| ix) | Vendor/ supplier to assume complete responsibility of a technically correct and safe installation. Vendor/ supplier is adviced to collect all the details/ facts from Owner/ PMC and visit site before quoting/ supplying. |  |  |
| x) | Vendor/ supplier to to study architectural drawings and visit site to findout suitability of DG sets shifting into basement/ (DG set room/ location) through ramps/ hatches etc. and confirm to owners/ PMC the suitability or otherwise before quoting/ before accpting order/ before supply of equipments. |  |  |

Annexure-1

AFFIDAVIT

- I, the undersigned, do hereby certify that all the statements made in the required statements are true & correct.

- The undersigned also hereby certifies that neither our firms M/s___________________ have abandoned any work in previous projects or in any other Department nor any contract awarded to us for such works have been rescinded, during last five years prior to the date of this bid.

- The undersigned understand and agrees that further qualifying information may be requested and agrees to furnish any such information at the request of the M/s Laxmi Niwas Mittal Institute of Information Technology (LNMIIT), Jaipur.

………………………………………………………..

(Signed by an Authorized Person of Firm)

………………………………………………

(Title of the Authorized Person)

…………………………………………….

(Name of Firm )

On non-judicial stamp paper of minimum Rs. 100/-)

Form of Bank Guarantee for Earnest Money Deposit /                     Performance Guarantee / Security Deposit

To

M/s LNM Institute of Information Technology,

Gram: Rupa ki Nangal,

Post: Sumel

Jaipur-302031

Rajasthan.

- In consideration of M/s Laxmi Niwas Mittal Institute of Information Technology (LNMIIT) – jointly established in 2002 by the state government of Rajasthan and the Lakshmi & Usha Mittal foundation, having its registered office at Gram: Rupa Ki Nangal, Post Sumel, Via Jamdoli, Jaipur, Rajasthan ( India ) – 302031  (hereinafter called “the Company” (which expression shall include its successor in business and assignees) have agreed to accept irrevocable bank guarantee of Rs……………………….( rupees………………….only ) valid upto……… (date) as Earnest Money Deposit from…………………( name and address of the “contractor”) for compliance of his obligations in accordance with the terms and conditions of the said NIT.

OR

In consideration of M/s Laxmi Niwas Mittal Institute of Information Technology (LNMIIT) – jointly established in 2002 by the state government of Rajasthan and the Lakshmi & Usha Mittal foundation, having its registered office at Gram: Rupa Ki Nangal, Post Sumel, Via Jamdoli, Jaipur, Rajasthan ( India ) – 302031  (hereinafter called “the Company” (which expression shall include its successor in business and assignees) have agreed to accept irrevocable bank guarantee of Rs……………………….( rupees………………….only ) valid upto……… (date) as Performance Guarantee/Security Deposit/Mobilisation Advance from the said contractor for compliance of his obligations in accordance with the terms and conditions of the agreement.

- We, ................ (Indicate the name of the bank) ..........................., (herein after referred to as “the Bank”), hereby undertake to pay to the COMPANY an amount not exceeding Rs ................................ (Rupees.............................................. only) on demand by the COMPANY within 10 days of the demand.

- We, ......................... (Indicate the name of the Bank) ................, do here by undertake to pay the amount due and payable under this guarantee without any demur, merely on a demand from the Government stating that the amount claimed is required to meet the recoveries due or likely to be due from the said Contractor. Any such demand made on the Bank shall be conclusive as regards the amount due and payable by the Bank under this Guarantee. However, our liability under this guarantee shall be restricted to an amount not exceeding Rs................... (Rupees ........................ only)

- We, .......................................(indicate the name of the Bank) ..................., further undertake to pay the Company any money so demanded notwithstanding any dispute or disputes raised by the contractor in any suit or proceeding pending before any Court or Tribunal, our liability under this Bank Guarantee being absolute and unequivocal. The payment so made by us under this Bank Guarantee shall be a valid discharge of our liability for payment there under and the Contractor shall have no claim against us for making such payment.

- We, ....................................(indicate the name of the Bank..............................., further agree that the Company shall have the fullest liberty without our consent and without affecting in any manner our obligation here under to vary any of the terms and conditions of the said agreement or to extend time of performance by the said Contractor from time to time or to postpone for any time or from time to time any of the powers exercisable by the Company against the said contractor and to forbear or enforce any of the terms and conditions relating to the said agreement and we shall not be relieved from our liability by reason of any such variation or extension being granted to the said Contractor or for any forbearance, act of omission on the part of the Company or any indulgence by the Company to the said Contractor or by any such matter or thing whatsoever which under the law relating to sureties would, but for this provision, have effect of so relieving us.

- We, ...................(indicate the name of the Bank) ........................................................ further agree that the Company at its option shall be entitled to enforce this guarantee against the Bank as a principal debtor at the first instance without proceeding against the Contractor and notwithstanding any security or other guarantee the Company may have in relation to the Contractor's liabilities.

- This guarantee will not be discharged due to the change in the constitution of the Bank or the Contractor.

- We, .......................................(Indicate the name of the Bank) ...................undertake not to revoke this guarantee except with the consent of the Company in writing.

- This Bank Guarantee shall be valid up to ...................................................... unless extended on demand by the Government. Notwithstanding anything mentioned above, our liability against this guarantee is restricted to Rs......................... (Rupees............................................................only) and unless a claim in writing is lodged with us within the date of expiry or extended date of expiry of this guarantee, all our liabilities under this guarantee shall stand discharged.

Date :…………….

Witnesses:

- Signature……….

Name and Address							Authorised signatory

Name ……….

Designation……..

Staff code No…….

Bank seal………..

- Signature……….

Name and Address

- Date to be worked out on the basis of validity period of 90 days where only financial bids are invited and 180 days for two/three bid system from the date of submission of tender.

- In paragraph 1, strike out the portion not applicable. Bank Guarantee will be made either for earnest money or for performance guarantee/security deposit/mobilization advance, as the case may be.

PRICE BID

(To be submitted separately in a sealed envelope on Company’s Letter Head )

Name of the Project: Construction of LNMIIT International Centre for Artificial intelligence (LICAI) (G+5) at Jaipur.

Sub Head: DG Set works.

| Sno. | Description | Amount |
| --- | --- | --- |
| 1.0 | SUPPLY of D.G. Set : |  |
| 1.1 | Item as described in serial no. 1.1 of the schedule of quantities (750kVA DG Set) |  |
| 1.2 | Item as described in serial no. 1.2 of the schedule of quantities (625kVA DG Set) |  |
| 2.0 | INSTALLATION TESTING AND COMMISSIONING OF ABOVE ITEMS. |  |
| 2.1 | Installation Testing and Commissioning of Item as described in serial no. 1.1 of the schedule of quantities and complete with Exhaust System ,Day tank piping etc .as per Specification .of (750kVA DG Set) |  |
| 2.2 | Installation Testing and Commissioning of Item as described in serial no. 1.2 of the schedule of quantities and complete with Exhaust System Day tank, piping etc. as per Specification mention in this document. (625kVA DG Set) |  |
| 3 | Comprehensive Maintenance |  |
| 3.1 | Comprehensive Maintenance for a period of next five years (05) after the completion of Defects Liability period of one year for serial no. 1 (1.1 ) |  |
| 3.2 | Comprehensive Maintenance for a period of next five years (05) after the completion of Defects Liability period of one year for serial no. 1 (1.2 ) |  |
|  | Total in Figures Including All |  |
|  | In Words: |  |

Date: - 								Seal & Signature.

Name: -

Designation: -

Place: -

Mobile No.: -