ADDENDUM TO NIT-2 ( SITC OF DG SETS) PRE-BID MEETING DT.10/03/2025

Mr. Puspendra Singh   				Mr. Gajendra Singh (Greaves)

Mr. Vipin Bansal 					Naveen Sharma (Sudhir)

Mr. Saroj Kumar dash				Kumar Amresh (Perfect)

Nishant Kiran Singh. (Perfect)

| QUERRIES | REPLY |
| --- | --- |
| Whether the OEM supposed to quote only Price bid as required in tender document for 5-year comprehensive maintenance. | Bidders to submit detailed bid as per tender. Financial bids asper format prescribed in tender. |
| About store, watch and ward of inward Equipment’s/ construction materials etc. of vendor. | Only space/place will be provided to the vendor, vendor to construct temp. store lock and key arrangement and for watch & ward only one person will be allowed to stay inside on duty at site with the arrangements of vendor. |
| Availability of construction power supply. | Construction power supply of approximately 5Kw load will be supply provided at a radius of 100meter. Vendor has to provide /connect necessary safety device to use the power supply on chargeable basis. A separate meter will be provided. |
| Availability Water at site. | Water will be available at site for Drinking Purpose for the Laboure free of cost. |
| Car policy | Vendors to arrange their own car policy for Machines/ and Labours |
| Sl. No. 6 (Payment terms) - .65% to corrected | It is to be read as 65% |
| Load Test at site | For load test (at site) The test will be carried out as specified in tender. How ever LNMIIT will arrange to provide load and diesel expenses for Load Test at Site only. |

| DG factory 110% load Test . | 100% load will be run for 6 hours and 30 minutes or as prescribed by OEM to witness the 110% load test for 30 minutes as described in this tender . |
| --- | --- |
| Extension of Last date for submission | Last date is extended to 5pm on 31st March2025 . |
| Drawings | Tentative Drawings are attached with addendum LNMIIT tender website and sent to vendors to in their mail IDs. |
| Accommodation for laboures | Vendors /contractors to arrange own accommodation for labor’s/staffs out side the campus . |

https://w-si.link/xHRFjQDu2ajOev2bR/ZW5naW5lZXIubWVwQGxubWlpdC5hYy5pbg