LIFE SAFETY/ FIRE DETECTION, DIGITAL VOICE EVACUATION SYSTEM

GENERAL DESCRIPTION

Provide Fire Detection and Alarm System in accordance with NFPA 72 (Latest edition) and requirements of the Contract Documents. Provide a complete operable and intelligent analog addressable Fire Alarm and Detection System with associated communication and notification systems. The system shall include interfaces for foreign systems, as described herein and in accordance with the Contract Documents, and all applicable Codes, Standards.

All Plant furnished shall be new and the latest state-of-the-art, products of a single Manufacturer engaged in the manufacturing of analog fire detection devices for at least 5 years.

All software licenses shall be supplied as part of the contract (If applicable). Renewable & subscription license is not acceptable.

The system shall be supplied, installed, tested, and approved by Engineer-In-Charge, and turned over to the Contractor in an operational condition.

The contractor shall contract with a single supplier for the fire alarm Plant, engineering, programming, inspection and tests, and shall provide a “UL Listing Certificate, FM/ EN-54Vds/ LPCB Approval” for the complete system.

Drawings: The Drawings shall serve to indicate the general arrangement of the various Plant and their generic functional interconnections. However, layout of Plant, accessories, specialties, conduit system and wiring, are diagrammatic and do not necessarily indicate every required device, fitting, etc., required for the complete installation.

SCOPE

A new intelligent reporting, microprocessor-controlled fire detection system shall be installed in accordance with the project specifications and drawings.

Basic Performance:

Alarm, trouble and supervisory signals from all intelligent reporting devices shall be encoded on NFPA Class A Signaling Line Circuits (SLC).

Initiation Device Circuits (IDC) shall be wired Class A (NFPA Style D) as part of an addressable device connected by the SLC Circuit.

Notification Appliance Circuits (NAC) shall be wired Class A (NFPA Style Z) as part of an addressable device connected by the SLC Circuit.

On Class A configurations a single ground fault or open circuit on the system Signaling Line Circuit shall not cause system malfunction, loss of operating power or the ability to report an alarm.

Alarm signals arriving at the FACP shall not be lost following a primary power failure (or outage) until the alarm signal is processed and recorded.

Speaker circuits shall be arranged such that there is a minimum of one speaker circuit per floor of the building or smoke zone whichever is greater.

Audio amplifiers and tone generating equipment shall be electrically supervised for normal and abnormal conditions.

NAC speaker circuits and control equipment shall be arranged such that loss of anyone (1) speaker circuit will not cause the loss of any other speaker circuit in the system. Two-way telephone communication circuits shall be supervised for open and short circuit conditions.

Basis of Design

An Intelligent Modular/ Expandable Fire Alarm System (IFAS) shall be provided to effect total control over the life safety services required in the building.

The system shall be provided with Addressable fire alarm initiating, annunciating and control devices.

The addressable and intelligent system shall be such that multi sensor detectors, beam detectors, manual call points, etc., can be identified with point address.

The FAS shall be able to recognize normal and alarm conditions, below normal sensor values that reveal trouble condition, and above normal values that indicate either an alarm condition or the need of maintenance.

Read-out or address an actual detector location. The operator shall also be able to adjust alarm and alarm thresholds and other parameters for the smoke sensors.

Provide a maintenance/ pre-alert/ fault alarm capability at smoke sensors to prevent the detectors from indicating a false alarm due to dust, dirt etc.

Provide alarm verification of individual smoke sensors. Systems that perform alarm verification on a zone basis shall not be acceptable. Alarm verification shall be printed on the printer at the Control Station’s printer to enhance system maintenance and identify possible problem areas.

Provide local numeric point address and LED display of device and current condition of the point.

Each detector shall use state-of-the-art Microprocessor Circuitry with error, detector self-diagnostics and supervision programs.

The detection of the fire shall be taken at the detector level.

Multi-Criteria Detectors shall be offered whereby the system logic activation is based on any three inputs from the detector i.e., smoke, fixed heat or rate of rise heat.

Provide outputs that are addressable, i.e., outputs shall have point address. The operator shall be able to command such points manually or assign the points to Logical Point Groups (Software Zones) for pre-programmed operation.

In the event of a fire alarm, but not in a fault condition, the following action shall be performed automatically.

- The System Alarm LED on the main fire alarm control panel shall flash.

- A local sounder shall be sounded.

- The LCD display on the main fire alarm control panel shall indicate all information associated with Fire Alarm condition including the type of alarm point and its location within the premises.

- Printing and history storage equipment shall log the information associated with the Fire Alarm Control Panel condition, along with the time and date of occurrence.

- All system output programs assigned via control-by-event programs that are to be activated by a particular point in alarm shall be executed, and the associated system outputs (alarm notification appliances and/or relays) shall be activated.

DRAWINGS & TECHNICAL SUBMITTALS

General

Two copies of all submittals shall be submitted to the Engineer-In-Charge for review.

All references to manufacturer's model numbers and other pertinent information herein are intended to establish minimum standards of performance, function and quality. Equivalent compatible UL-listed equipment from other manufacturers may be substituted for the specified equipment as long as the minimum standards are met.

For equipment other than that specified, the Contractor shall supply proof that such substitute equipment equals or exceeds the features, functions, performance, and quality of the specified equipment.

Shop Drawings

Sufficient information, clearly presented, shall be included to determine compliance with drawings and specifications.

Include manufacturer's name(s), model numbers, ratings, power requirements, equipment layout, device arrangement, complete wiring point-to-point diagrams, and conduit layouts.

Show annunciator layout, configurations, and terminations.

Manuals

Submit simultaneously with the shop drawings, complete operating and maintenance manuals listing the manufacturer's name(s), including technical data sheets.

Wiring diagrams shall indicate internal wiring for each device and the interconnections between the items of equipment.

Provide a clear and concise description of the operation that gives, in detail, the information required to properly operate the equipment and system.

Software Modifications

Provide the services of a factory trained and authorized technician to perform all system software modifications, upgrades or changes. Response time of the technician to the site shall not exceed 4 hours.

Provide all hardware, software, programming tools and documentation necessary to modify the fire alarm system on site. Modification includes addition and deletion of devices, circuits, zones and changes to system operation and custom label changes for devices or zones. The system structure and software shall place no limit on the type or extent of software modifications on-site.

Certifications

Together with the shop drawing submittal, submit a certification from the major equipment manufacturer indicating that the proposed supervisor of the installation and the proposed performer of contract maintenance is an authorized representative of the major equipment manufacturer. Include names and addresses in the certification.

WARRANTY

All work performed and all material and equipment furnished under this contract shall be free from defects and shall remain so for a period of at least one (1) year from the date of acceptance. The full cost of maintenance, labor and materials required to correct any defect during this one-year period shall be included in the submittal bid.

POST CONTRACT MAINTENANCE

Complete maintenance and repair service for the fire alarm system shall be available from a factory trained authorized representative of the manufacturer of the major equipment for a period of five (5) years after expiration of the guaranty.

As part of the bid/ proposal, include a quote for a maintenance contract to provide all maintenance, tests, and repairs described below. Also include a quote for unscheduled maintenance/ repairs, including hourly rates for technicians trained on this equipment, and response travel costs for each year of the maintenance period. Submittals that do not identify all post contract maintenance costs will not be accepted. Rates and costs shall be valid for the period of five (5) years after expiration of the guaranty.

Maintenance and testing shall be on a semiannual basis or as required by the client. A preventive maintenance schedule shall be provided by the Contractor describing the protocol for preventive maintenance. The schedule shall include:

Systematic examination, adjustment and cleaning of all detectors, manual fire alarm stations, control panels, power supplies, relays, and water flow switches and all accessories of the fire alarm system.

Each circuit in the fire alarm system shall be tested semiannually.

Each smoke detector shall be tested in accordance with the requirements of NFPA 72 Chapter 7.

POST CONTRACT EXPANSIONS

The Contractor shall have the ability to provide parts and labor to expand the system specified, if so requested, for a period of five (5) years from the date of handover.

As part of the submittal, include a quotation for all parts and material, and all installation and test labor as needed to increase the number of intelligent or addressable devices by ten percent (10%). This quotation shall include intelligent smoke detectors, intelligent heat detectors, addressable manual stations, addressable monitor modules and addressable modules equal in number to one tenth of the number required to meet this specification (list actual quantity of each type).

The quotation shall include installation, test labor, and labor to reprogram the system for this 10% expansion. If additional FACP hardware is required, include the material and labor necessary to install this hardware.

Submittals that do not include this estimate of post contract expansion cost will not be accepted.

APPLICABLE STANDARDS AND SPECIFICATIONS

The specifications and standards listed below form a part of this specification. The system shall fully comply with the latest issue of these standards, if applicable.

National Fire Protection Association (NFPA) - USA:

NFPA 13	Sprinkler Systems

NFPA 16	Foam/ Water Deluge and Spray Systems

NFPA 17	Dry Chemical Extinguishing Systems.

NFPA 17A	Wet Chemical Extinguishing Systems

NFPA 2001	Clean Agent Extinguishing Systems

NFPA 70,	National Electrical Code

NFPA 72	National Fire Alarm Code

NFPA 76	Telecommunication Facilities

NFPA 318	Clean Room Applications

NFPA 101	Life Safety Code

NFPA 90A	Air conditioning & ventilation system

Underwriters Laboratories Inc. (UL) – USA:

UL-50 		Cabinets and Boxes

UL-268	Smoke Detectors for Fire Protective Signalling Systems

UL-864	Control Units for Fire Protective Signalling Systems

UL-268A	Smoke Detectors for Duct Applications

UL-521	Heat Detectors for Fire Protective

UL-228	Door Closers-Holders for Fire Protective Signalling Systems

UL- 464	Audible Signalling Appliances

UL-38		Manually Actuated Signalling Boxes

UL-346	Water-flow Indicators for Fire Protective Signalling Systems

UL-1481	Power supplies for Fire Protective Signalling Systems.

UL-1076	Control Units for Burglar Alarm

UL-1971	Visual Notification Appliances

UL-318	Clean Room Application (9th Edition)

NATIONAL BUILDING CODES/ IS CODES

The Video Display Terminal (VDT) shall comply with Swedish magnetic emission and X-radiation guidelines MPR 1990:10.

APPROVALS:

- UL listing

- ULC listing

- FM approval

The system shall have proper listing and/or approval from the following nationally recognized agencies:

UL Underwriters Laboratories Inc (9thEdition)

The fire alarm control panel shall meet UL Standard 864 9th Edition.

The system shall be listed by the national agencies as suitable for extinguishing release applications. The system shall support release of high and low pressure gases.

GENERIC SYSTEM CAPABILITIES

## Analogue addressable microprocessor-based fire alarm system with initiating devices, notification appliances, monitoring and control devices as indicated on the drawings and as specified herein.

## The system shall be capable of on-site programming to accommodate system expansion and facilitate changes in operation.

## All software operations shall be stored in a non-volatile programmable memory within the fire alarm control unit. Loss of primary and secondary power shall not erase the instructions stored in memory.

## Panels shall be capable of full system operation during new site-specific configuration download.

## Remote panel site-specific software and executive firmware downloads shall be capable of being performed over proprietary fire alarm network communications and via TCP/ IP Ethernet network communications. Ethernet access to any fire alarm panel shall be capable of providing access only to authenticated users through a cryptographically authenticated and secure SSL tunnel.

## Panels shall automatically store all program changes to the panel’s non-volatile memory each time a new program is downloaded. Panels shall be capable of storing the active site-specific configuration program and no less than 9 previous revisions in reserve. A compare utility program shall also be available to authorized users to compare any two of the saved programs. The compare utility shall provide a deviation report highlighting the changes between the two compared programs.

## Panels shall provide electronic file storage with a means to retrieve a record copy of the site-specific software and up to 9 previous revisions. Sufficient file storage shall be provided for other related system documentation such as record drawings, record of completion, owner’s manuals, testing and maintenance records, etc.

## The media used to store the record copy of site-specific software and other related system documentation shall be electrically supervised. If the media is removed a trouble shall be reported on the fire alarm control panel.

## The system shall provide a means to recall alarms and trouble conditions in chronological order for the purpose of recreating an event history. A separate alarm and trouble log shall be provided.

REMOTE ACCESS

- Fire Alarm Control Panel (FACP) shall have the capability to provide a remote service access feature using Ethernet and TCP/ IP communications protocol. The Remote Access feature shall provide automatic notification of system faults and remote diagnostics of system status for responding technicians prior to arrival on site.

- The internet remote access service function shall provide automated real time off-site reporting of discrete system events to a remote service support center with details of internal FACP fault conditions allowing a pre-site visit analysis of repair requirements.

- Existing FACP controls shall be capable of retrofitting the Remote Service module as a plug-in upgrade feature.

- The remote service network shall work on the customers Ethernet infrastructure and be Fire-Wall friendly for two-way communications for off-site reporting. The feature shall be compatible with existing proxy servers and firewalls shall not require any special changes or modifications.

- The remote service system shall be a non-Windows based application to protect against conventional virus attacks.

- The remote service system shall be compatible with virtual LANS (VLAN).

- The remote service system shall work on an outbound communication premise (panel calls home) in order to eliminate the possibility of any inbound connection into the network (from trusted or non-trusted sites).

- The remote service system shall have capability to provide an audit trail of all events and service connections.

- The FAS shall be compatible to Remote Service program that provides the following requirements if asked for:

24/7 recording of FACP service activity

Off-site diagnostics by a technical specialist to provide repair and parts guidance to the service technician prior to a site visit.

NETWORK COMMUNICATION

- Network node communication shall be through a token ring, hub, or star topology configuration, or combination thereof.

- A single open, ground or short on the network communication loop shall not degrade network communications. Token shall be passed in opposite direction to maintain communications throughout all network nodes. At the same time the status of the communication link shall be reported.

- If a group of nodes becomes isolated from the rest of the network due to multiple fault conditions, that group shall automatically form a sub-network with all common interaction of monitoring and control remaining intact. The network shall be notified with the exact details of the lost communications.

- Fiber optics communication shall be provided as an option via a fiber optics modem. Modem shall multiplex audio signals and digital communication via full duplex transmission over a single fiber optic cable, either single mode or multi-mode.

- The communication method shall be in accordance to NFPA 72 style 7.

- Network communication shall be “Peer-to-Peer” and the complete or filtered event indication shall be possible in keeping with the system architecture and requirements of this document.

- Initiating device signals, voice signals and cause-n-effect logic shall travel in seamless and hassle-free manner over the FDA network communication channel and even the worst condition load/ full load shall keep the response time within the limit specified by NFPA-72/ 2013 edition.

REQUIRED FUNCTIONS

- Operator Console/ HMI: The operator console/ HMI shall offer the means to display, monitor and control all the ALARM, TROUBLE and SUPERVISORY signals from the initiating devices connected to the FACP. The operator console/ HMI shall meet the specifications mentioned for it under “Product Specification” part of this document.

- Annunciation: Operation of ALARM, TROUBLE and SUPERVISORY initiating devices shall be annunciated at the FACP and the Remote Annunciator indicating the type of device, the operational state of the device (Alarm, Trouble or Supervisory) and shall display the custom label associated with the device.

- Priority of Signals: Fire Alarm events shall have highest priority. Subsequent alarm events are queued in the order received and do not affect existing alarm conditions. Priority Two, Supervisory and Trouble events have second, third, and fourth-level priority, respectively. Signals of a higher-level priority take precedence over signals of lower priority even though the lower-priority condition occurred first. However, all the events shall be annunciated regardless of priority or order received.

- Noninterfering signals: An event on one zone does not prevent the receipt of signals from any other zone. All zones are manually resettable from the FACP after the initiating device or devices are restored to normal. The activation of an addressable device does not prevent the receipt of signals from subsequent addressable device activations.

- Alarm: A system alarm shall include:

- Indication of alarm condition at the FACP and at the annunciators.

- Identification of the device/ zone triggering alarm at the FACP and the annunciators.

- Operation of audible and visible notification appliances until silenced at FACP.

- Selectively closing doors normally held open by magnetic door holders on the fire floor, floor above and floor below.

- Unlocking designated doors.

- Shutting down supply and return fans serving zone where alarm is initiated.

- Closing smoke dampers on system serving zone where alarm is initiated.

- Initiation of smoke control sequence as defined.

- Transmission of signal to the supervising station.

- Alarm Silencing: If the "Alarm Silence" button is pressed, all audible signals shall cease operation. The visible signals shall be off at Panel Reset.

- System Reset: System Reset shall do the following

- The "System Reset" button shall be used to return the system to its normal state. Display messages shall provide operator assurance of the sequential steps ("IN PROGRESS", "RESET COMPLETED") as they occur. The system shall verify all circuits or devices are restored prior to resetting the system to avoid the potential for re-alarming the system.  The display message shall indicate "ALARM PRESENT, SYSTEM RESET ABORTED."

- Should an alarm condition continue, the system will remain in an alarmed state.

- Supervisory Operations: Upon activation of a supervisory device such as a fire pump power failure, low air pressure switch, and tamper switch, the system shall operate as follows

- Activate the system supervisory service audible signal and illuminate the LED at the control unit and the remote annunciator.

- Pressing the Supervisory Acknowledge Key will silence the supervisory audible signal while maintaining the Supervisory LED "on" indicating off-normal condition.

- Record the event in the FACP historical log.

- Transmission of supervisory signal to the supervising station.

- Restoring the condition shall cause the Supervisory LED to clear and restore the system to normal.

- Evacuation (Drill) Switch: Evacuation/ Drill Switch shall be provided to operate the notification appliances without causing other control circuits to be activated.

- Walk Test: The system shall have the capacity of 8 programmable passcode protected one person testing groups, such that only a portion of the system need be disabled during testing.  The actuation of the "enable one person test" program at the control unit shall activate the "One Person Testing" mode of the system as follows:

- The city circuit connection and any suppression release circuits shall be bypassed for the testing group.

- Control relay functions associated with one of the 8 testing groups shall be bypassed.

- The control unit shall indicate a trouble condition.

- The alarm activation of any initiating device in the testing group shall cause the audible notification appliances assigned only to that group to sound a code to identify the device or zone.

- The unit shall automatically reset itself after signaling is complete.

- Any opening of an initiating device or notification appliance circuit wiring shall cause the audible signals to sound for 4 seconds indicating the trouble condition.

- Spoken Walk Test: In case the system is equipped with Integrated Voice Evacuation and Public Address System, the Walk Test shall have an option to notify the findings of each device through voice notification.

- Install Mode: The system shall provide the capability to group all non-commissioned points and devices into a single "Install Mode" trouble condition allowing an operator to clearly identify event activations from commissioned points and devices in occupied areas.

It shall be possible to individually remove points from Install Mode as required for phased system commissioning.

It shall be possible to retrieve an Install Mode report listing that includes a list of all points assigned to the Install Mode. Panels not having an install mode shall be reprogrammed to remove any non-commissioned points and devices.

- Service Gateway: The system shall be compatible with a service gateway as described. If asked for a Service Gateway software application shall be provided that allows an authorized service person to remotely query panel status during testing, commissioning, and service without the need to return to the panel using standard email/ Instant Messaging Tools/ Smart Phones/ Tablets/ I Pads etc.

Fire Alarm Control Panel (FACP)

- Comply with UL 864, "Control Units and Accessories for Fire Alarm Systems". The following FACP hardware shall be provided:

- Power Limited base panel with Platinum/ Red cabinet and door, 240 VAC input power.

- 2,000-point capacity where (1) point equals (1) monitor (input) or (1) control (output).

- 2,000 points of Network Annunciation at FACP Display when applied as a Network Node

- 2000 points of annunciation where one (1) point of annunciation equals:

- 1 LED driver output on a graphic driver or 1 switch input on a graphic switch input module.

- 1 LED on panel or 1 switch on panel.

- Fire Alarm Control Panel is able to connect per loop 250 devices Detector or Module in any combination to keep flexibility remains at site.

- Panel shall include 854 character/ Touch Screen approx. 6”, expanded content multi-line QVGA LCD display.

- Municipal City Circuit Connection with Disconnect switch, 24V DC Remote Station (reverse polarity), local energy, shunt master box, or a form "C" contact output.

- One Auxiliary electronically resettable fused 2A @24V DC Output, with programmable disconnect operation for 4-wire detector reset.

- One Auxiliary Relay, SPDT 2A @24 - 32VDC, programmable as a trouble relay, either as normally energized or de-energized, or as an auxiliary control.

- Three (3) Class B or A (Style Y/Z) Notification Appliance Circuits (NAC; rated 3A@24VDC, resistive).

- Where required provide Intelligent Remote Battery Charger for charging up to 110Ah batteries.

- Power Supplies with integral intelligent Notification Appliance Circuit [Class B] [Class A] for system expansion.

- Four (4) form "C" Auxiliary Relay Circuits (Form C contacts rated 2A @ 24VDC, resistive), operation is programmable for trouble, alarm, supervisory of other fire response functions. Relays shall be capable of switching up to ½ A @ 120VAC, inductive.

- The FACP shall support up to (5) RS-232-C ports and one service port. All (5) RS-232 Ports shall be capable of two-way communications.

- Remote Unit Interface: supervised serial communication channel for control and monitoring of remotely located annunciators and I/O panels.

- Modular Network Communications Card.

- Programmable DACT for either Common Event Reporting or per Point Reporting.

- Service Port Modem for dial in passcode access to all fire control panel information.

- Microprocessor based Fire Alarm Control Panel (FACP) with 80 characters displaying at least 600 or more characters in multiple lines at a time and shall accommodate the no. of detection loops and the quantity of field devices mentioned in the commercial BOQ. The HMI shall have at least 5 or more customer programmable buttons with LED indication in order to freely configure its programmed response as per project requirement.

- Each Detection Loop of FACP shall accommodate, monitor and control a minimum of 250 intelligent addressable devices in any combination. The exact combination of the field devices in a detection loop shall be at the discretion of the design consultant based on the project requirement & System Design. However, the System Proposed by the Solution Provider/ System Integrator shall accommodate all the field devices/ components and shall meet all the requirements.

- FACP shall connect all the field devices (Detectors, MCPs, Control Modules, Monitor Modules, Hooter cum Strobes etc.), shall fully monitor them and communicate to them for their status and shall be able to take intelligent decision of ALARM, TROUBLE, SUPERVISORY based on the programmed cause-n-effect logic. It should have an interactive HMI (display cum operation interface), with status monitoring LEDs for AC Power, Fire Alarm, System Trouble, System Supervisory, Ground Fault and shall have at least 5 programmable switches with LED for seamless operation & maintenance.

- FACP shall be UL and ULC listed, and FM approved.

- FACP shall comply to UL-864 9th edition.

- FACP shall have a dedicated mass storage memory to store project related critical back-up like Auto-CAD as-built drawings, reports, logs, customer-text files etc. in line with NFPA-72, 2013 requirements. The memory shall be fully monitored by the FACP CPU and shall be password protected.

- FACP shall support multiple System Power Supplies and Expansion Power Supplies in cascade to ensure the optimum power as required by the system load and system design.

- Each power supply shall provide total of 9 Amp current out of which 2 Amp per NAC shall be dedicated to the current requirement of Notification Appliance Circuit.

- FACP shall house 2 nos. of 50 AH batteries in its own housing and shall have the proper, trouble-free charging capacity for them. However, the FACP shall be able to charge up to 110AH of batteries if required by the system design and system load.

- FACP shall have the networking capability with the other control panels of same family by adding a network module.

- FACP shall be compatible to Modbus over RS-232, Modbus over RS-485, Modbus over IP and BACnet over IP as different open protocol variants for 3rd party Integration. Exact variant and module shall be considered as mentioned in commercial BOQ. The selection of exact protocol variant shall be at sole discretion of the design consultant based on the project & system requirement. Any deviation in this regard needs prior formal approval of the design consultant.

- FACP shall be compatible to seamless integration of aspiration system via application specific interface module. The FACP shall be able to view, monitor and control the aspiration system from its HMI.

- FACP shall have peak value logging capability and shall be able to analyse the peak value of individual sensors for individual sensitivity selection.

- FACP shall provide min 5 or more RS-232 ports for printers and other serial port utilities.

- FACP shall have IP communication capability.

- FACP shall have battery brackets for seismic area protection.

- FACP shall support the intelligent Cause-n-Effect programming based on the Boolean logic or equivalent to ensure the achievement of complete system functionality as required by this document.

- FACP shall be capable of indicating different events of varying priority and shall be able to map those events in intelligent cause-n-effect logic to achieve “Positive Alarm Sequence” and notification activation & deactivation as required by “Cause-n-Effect” programming. The exact requirement of cause-n-effect will depend at sole discretion of design consultant in line with the code requirement and protected premise requirement.

- FACP shall be capable of delivering all the functionalities mentioned under “Required Functions” of this document in “General Specification” part.

- FACP shall support priority setting of various events.

- FACP shall support the password protected authority level & assignment.

- FACP shall have forward and backward compatibility with various generations of devices in its family to protect client’s investment.

- FACP shall support distributed architecture/ arrangement for the components of the same control panel/ Network Node where it shall allow the mounting of various components like analogue addressable detection loop interfaces, amplifiers, fire fighter telephones, power supplies and other accessories in multiple remote enclosures at different locations away from the main FACP to facilitate effective and efficient field wiring terminations, avoid unnecessary cable runs. However, the functionality of the FACP shall be intact. A single communication failure between FACP and remote enclosures shall not affect any system performance (but report the trouble condition at FACP) and complete communication failure (by multiple discontinuities or short-circuits) of a remote enclosure shall enable it to operate as a conventional system and report the complete status of the trouble at the FACP.

- FACP shall be UL & ULC listed, and FM approved.

Voice Alarm

Provide an emergency communication system, integrated with the FACP, including voice alarm system components, microphones, amplifiers, and tone generators. Features include:

Amplifiers comply with UL 1711, "Amplifiers for Fire Protective Signaling Systems." Amplifiers shall provide an onboard local mode temporal coded horn tone as a default backup tone. Test switches on the amplifier shall be provided to test and observe amplifier backup switchover.

Each amplifier shall communicate to the host panel amplifier and NAC circuit voltage and current levels for display on the user interface. Each amplifier shall be capable of performing constant supervision for non-alarm audio functions such as background music and general paging.

Dual alarm channels permit simultaneous transmission of different announcements to different zones or floors automatically or by use of the central control microphone.] [none] All announcements are made over dedicated, supervised communication lines. All risers shall support [Class A]/ [Class B] wiring for each audio channel.

Eight channel digitally multiplexed audio for systems that require more than two channels of simultaneous audio. Up to 8 channels of audio shall be multiplexed Class A twisted pair.

Emergency voice communication audio controller module shall provide up to 32 minutes of message memory for digitally stored messages. Provide supervised connections for master microphone and up to 5 remote microphones.

Status annunciator indicating the status of the various voice alarm speaker zones and the status of fire fighter telephone two-way communication zones.

When required, Redundant Voice Command Centers shall be capable of generating voice paging from more than one node in a network audio system.

Evacuation System

Non-Alarm Audio: The fire alarm control panel shall provide non-alarm audio from paging and/or music source over the fire alarm evacuation speakers. This feature shall be an integral part of the fire alarm system and shall use some or all the audio components from the fire alarm evacuation system.

The fire alarm system and the non-alarm audio operation shall comply with NFPA 72 requirements for non-emergency purposes at a fire command center that is not constantly attended by a trained operator.

All fire alarm system hardware and software shall be U.L. listed for non-alarm audio use. The fire alarm system shall supervise for system hardware and field wiring faults while playing non-alarm audio over the evacuation speakers. Any hardware failure or speaker circuit fault detected when the system is playing non-alarm audio shall report a trouble on the fire alarm control panel. All audio components used for both the non-alarm audio and the fire alarm evacuation system shall be manufactured by the same supplier.

The non-alarm audio shall have two dedicated audio inputs to the fire alarm control panel. Terminal strip connections and an industry standard RCA receptacle shall be provided at the fire alarm control panel for terminating the audio source. The fire alarm input shall be 600-Ohm impedance. The inputs on the fire alarm control panel shall be electrically isolated via an isolation transformer.

The fire alarm control panel shall accept industry standard "line level audio input" from the non-alarm audio source. The fire alarm system hardware and software shall distribute the audio over the fire alarm evacuation speakers. The selection of which speaker zones to distribute the non-alarm audio to the building occupants shall be coordinated.

The fire alarm control panel shall be able to make audio input level adjustments from the non-alarm audio source. This adjustment will match the non-alarm audio source to the fire alarm input. After the audio levels are adjusted, control the volume level from the non-alarm audio source.

The fire alarm system will provide "buttons" have the capability to provide operator "buttons" that will adjust the volume level of pre-assigned non-alarm audio zones. The volume level of non-alarm audio that is being broadcast to any audio zone will also be individually adjustable by time of day via a pre-specified schedule.

The non-alarm audio shall be the lowest priory audio on the fire alarm system. The non-alarm audio shall not interfere with any of the fire alarm emergency signals that may include live voice, pre-recorded emergency voice messages, or any alert tones. Switches shall be located on the fire alarm control panel to turn on or off the non-alarm audio system feature. The fire alarm control panel shall have LED lamps to indicate the ON vs. OFF status of the non-alarm audio feature. Speaker circuits that are actively broadcasting non-alarm audio will also be indicated by LEDs.

The non-alarm audio shall be synchronized throughout the fire alarm life safety system amplifiers and speaker circuits. Any remote amplifier panels located on the fire alarm system network shall also be synchronized. The system shall be capable of accepting a system-wide non-alarm audio input at the main fire alarm control or another local non-alarm audio input at a remote amplifier panel to serve only the areas served by that remote panel.

Multiple non-alarm audio sources must be accessible by the fire alarm non-alarm audio system. Each separate non-alarm audio source will have the ability to be broadcast into a distinct fire zone, depending on occupant preference. Any system restricted to a limited number of non-audio sources will not be accepted.

The system must have the capability of broadcasting an unlimited number of non-alarm sources, except as determined by the number of individual fire zones served by the fire alarm system.

Non-alarm audio shall be automatically turned off in the event of primary power failure to the fire alarm control panel or any of the remote amplifier panels controlled by the main fire alarm control panel.

Fire fighters' telephone communication system: Arrange system to use dedicated, two-way, supervised voice communication links between the FACP and remote fire fighters' telephone stations throughout the building.

Distributed Module Operation: FACP shall be capable of allowing remote location of the following modules: interface of such modules shall be through a [Style 7 (Class A)]/ [ Style 4 (Class B)] supervised serial communications channel (SLC):

Amplifiers, voice and telephone control circuits

Addressable Signaling Line Circuits

Initiating Device Circuits

Notification Appliance Circuits

Auxiliary Control Circuits

Graphic Annunciator LED/ Switch Control Modules

In systems with two or more Annunciators and/or Command Centers, each Annunciator/ Command Center shall be programmable to allow multiple Annunciators/ Command Centers to have equal operation priority or to allow hierarchal priority control to be assigned to individual Annunciator/ Command Center locations.

Cabinet: Lockable steel enclosure. Arrange unit so all operations required for testing or for normal care and maintenance of the system are performed from the front of the enclosure. If more than a single unit is required to form a complete control unit, provide exactly matching modular unit enclosures.

Alphanumeric Display and System Controls: Panel shall include 854 characters, expanded content multi-line QVGA LCD display to indicate alarm, supervisory, and component status messages and shall include a keypad for use in entering and executing control commands.

The system shall include the necessary hardware to provide expanded content, multi-line, operator interface displays as indicated on the drawings and specifications. The expanded content multi-line displays shall be Quarter-VGA (QVGA) or larger and be capable of supporting a minimum of 854 char/ Approx 6” Touch Screen standard ASCII characters to minimize or eliminate the levels of navigation required for access to information when responding to critical emergencies and abnormal system conditions. The QVGA operator interface shall provide operator prompts and six contexts sensitive soft keys for intuitive operation.

Expanded content, multi-line operator interfaces shall be capable of providing the following functions:

Dual language operation with Instant-Switch language selection during runtime.

Activity display choices for:

First 8 Events

First 5 Events and Most Recent Event (with first and most recent event time and date stamps). First Event and Most Recent Event (with first and most recent event time and date stamps). Scrollable List Display [displays a scrollable list of active points for the event category (alarm, priority 2, supervisory, or trouble) selected. The position in this list will be the last acknowledged point (not flashing) at the top followed by the next 7 unacknowledged points (flashing)].

General Event Status (alarm, priority 2, supervisory, or trouble in system)

Site Plan

Equal or hierarchal priority assignment. In systems with two or more operator interfaces, each operator interface shall be programmable to allow multiple operator interfaces to have equal operation priority or to allow hierarchal priority control to be assigned to individual operator interfaces (locations).

Up to 50 custom point detail messages for providing additional point specific information in detailed point status screens.

Bitmap file import for operator interface display of site plan and background watermark images.

Expanded content, multi-line displays shall [have the capability] include the necessary hardware and software] to provide Dual-Language operation.

Language selection shall be via a switch on the operator interface panel. Operator interface panels shall support instant-language-switchover during runtime to allow the operator to toggle between languages each time the language selection switch is operated, without requiring complicated multi-step processes.

Both one-byte and two-byte characters shall be supported.

Smoke Control System

Smoke Control System: Provide a smoke control system which is UL 864 listed for smoke control system service. The system shall provide automatic operation of smoke exhaust fans, makeup air fans, air handling units, and dampers in accordance with the smoke control sequence indicated on the drawings. The smoke control system shall be located in the fire command center.

Provide and install smoke control relays within 3 feet of each smoke exhaust fan controller, makeup air fan controller, air handling unit’s controller, and damper controlled by the smoke control system. The building automation/ temperature control system shall terminate the relays to the fan controllers, air handling unit controllers, and dampers.

Provide and install addressable modules to monitor status/ operation of each smoke exhaust fan, makeup air fan, air handling unit, and damper controlled by the smoke control system. The fire alarm contractor shall terminate the modules to status indicators.

Enclosure: Finish to match Fire Alarm Control Units. The locking cover/ display assembly is hinged on the left. Key and lock shall be common to all secured fire alarm system enclosures.

Carbon Monoxide Sensor:

Carbon Monoxide (CO) detector detects CO concentrations in the air at or below the UL 2034 sensitivity limits for CO exposure and before symptoms of CO exposure appear, it alerts to FAP by using interface module and alert through audible and visual alarm.

The CO detectors shall have three color visual LED display indicates status and contamination level. A green display indicates the detector is operating normally. An amber display indicates a system trouble. A red display indicates dangerous CO levels.

Fire Fighters' Telephones

Telephone Handsets: High-impact plastic handset, heavy-duty coil cord, and hook switch; connected to the FACP by means of dedicated, supervised communication lines. Handsets have a dynamic receiver and a carbon transmitter, operating on 24VDC.

A black master telephone handset with a push to talk button and a flexible-coiled self-winding five (5) foot cord shall be provided and recessed within a protective unit-mounted enclosure at the command center.

Cabinet: Flush- or surface-mounted as indicated, 18-gage, minimum, painted steel with a latched hinged door with trim labeled "Fire Fighters' Phone." Size to accommodate handset and cord.

Remote CRTs, PC Annunciator and Printers

Fire Alarm Control Unit shall be capable of operating remote CRT's and/or printers; output shall be ASCII from an RS-232-C connection with an adjustable baud rate.

Fire Alarm Control Unit shall be capable of operating an Agency Listed PC Annunciator Client/ Server which provides status annunciation and limited system control using a convenient and familiar Microsoft Vista Business operating system-based interface. Other compatible Operating Systems shall include Microsoft XP Professional and Windows® 2000 Professional. The PC Annunciator Client/ Server shall provide the following functions:

Login/ logout password protection with time duration selectable automatic logout.

Display Alarm, Supervisory, Priority 2, and Trouble conditions with numerical tallies for each.

Display first and last alarms.

Different event types have separate visible indicators with a common audible indicator.

Event logs can be searched and printed.

View and/or print True Alarm status reports and service reports. (Printing requires an available local or network printer).

Alarm Silence: System Reset; and Priority 2 Reset.

Global and individual point acknowledge.

Set system time and date and clear event log.

Individual point access for control or parameter revisions.

WALKTEST system test is supported for service convenience.

Up to (8) Simultaneous Client connections shall be supported by the PC Annunciator Server. Remote Clients shall be capable of connecting to the PC Annunciator Server via Ethernet LAN/ WAN connections.

Each RS-232-C port shall be capable of supporting and supervising a remote Printer, CRT/ Keyboard, or PC Annunciator; the FACP shall support as many as five (5) remote RS-232 devices. The Fire Alarm Control Panel shall support five (5) RS-232-C ports.

Remote LCD Annunciator

Provide a remote LCD Annunciator with the same "look and feel" as the FACP operator interface. The Remote LCD Annunciator shall use the same Primary Acknowledge, Silence, and Reset Keys; Status LEDs and LCD Display as the FACP.

Annunciator shall have super-twist LCD display. Annunciator shall be provided with four (4) programmable control switches and associated LEDs.

Under normal conditions the LCD shall display a "SYSTEM IS NORMAL" message and the current time and date.

Should an abnormal condition be detected the appropriate LED (Alarm, Supervisory or Trouble) shall flash. The unit audible signal shall pulse for alarm conditions and sound steady for trouble and supervisory conditions.

The LCD shall display the following information relative to the abnormal condition of a point in the system:

Type of device (e.g., smoke, pull station, waterflow).

Point status (e.g., alarm, trouble).

Operator keys shall be key switch enabled to prevent unauthorized use. The key shall only be removable in the disabled position. Acknowledge, Silence and Reset operation shall be the same as the FACP.

Remote 854 Char/ Approx 6” Touch Screen QVGA LCD Annunciator

Provide a remote 854 char/ Approx 6” Touch Screen, QVGA LCD enunciator, with the same "look and feel" as the FACP operator interface. The Remote QVGA LCD Annunciator shall use the same Primary Acknowledge, Silence, and Reset Keys as the FACP.

The QVGA Annunciator shall have an expanded content, multi-line display capable of supporting a minimum of 854 standard ASCII characters/ 5.7” Touch Screen to minimize or eliminate the levels of navigation required for access to information when responding to critical emergencies and abnormal system conditions. The QVGA Annunciator shall provide:

Operator prompts and six contexts sensitive soft keys for intuitive operation.

Seven (7) programmable control switches and associated LEDs.

Three (3) programmable general-purpose LEDs.

Capability of supporting Dual Languages with Instant-Switchover between languages in runtime operation.

Support for both one-byte and two-byte characters.

Under normal conditions the QVGA LCD shall display [a "SYSTEM IS NORMAL" message, the current time and date, and the quantity of abnormal status conditions for each event category (i.e., fire alarm, priority 2, supervisory, and trouble)] [ with a watermark background image] [a site plan of the facility layout] [with status icons to indicate area status for highest priority active events].

The QVGA Annunciator shall be programmable for the following Activity display choices:

First 8 Events.

First 5 Events and Most Recent Event with First and Most Recent event time and date stamps.

First Event and Most Recent Event with First and Most Recent event time and date stamps.

Scrollable List Display [displays a scrollable list of active points for the event category (alarm, priority 2, supervisory, or trouble) selected. The position in this list will be the last acknowledged point (not flashing) at the top followed by the next 7 unacknowledged points (flashing)]. General Event Status (Alarm, Priority 2, Supervisory, or Trouble in system).

Site Plan with optional status icons to indicate area status for highest priority active events.

Should an abnormal condition be detected the appropriate LED (Alarm, Priority 2, Supervisory or Trouble) shall flash. The unit audible signal shall pulse for alarm conditions and sound steady for trouble and supervisory conditions.

The QVGA LCD shall display the following minimum information relative to the abnormal condition of a point in the system:

854-character custom location label.

Type of device (e.g., smoke, pull station, waterflow).

Point status (e.g., alarm, trouble).

QVGA Annunciators shall be protected from unauthorized use via a locked door or equivalent means. In addition, in systems with two or more Annunciators, each Annunciator shall be programmable to allow multiple Annunciators to have equal operation priority or to allow hierarchal priority control to be assigned to individual Annunciators (locations). Acknowledge, Silence and Reset operation shall be the same as the FACP.

Network Annunciators

Network Display Unit shall contain the following features:

- LCD display to indicate alarm, supervisory, and component status messages and shall include a keypad for use in entering and executing control commands.

- Capacity to annunciate 12,000 network points and/or point lists.

- Historical event logs shall maintain separate 600 Alarm and 600 Trouble events.

- The network shall provide a means to log into any node on the system via a laptop computer or CRT/ Keyboard and have complete network access (Set Host) for diagnostics, maintenance reporting, and information gathering of all nodes in the system. Systems not meeting this requirement must provide all diagnostic tools required to support this function from selected points on the network.

Graphical Software Workstation

The Graphical Workstation shall consist of:

Fire Graphic Software

- Graphic Software must be UL 864 Listed and work as per UL-54 norms of fire Alarm System.

- The proposed software should be from the same manufacture of fire alarm system & should be UL & FM approved.

- To provide Annunciation, Status display, Monitoring & Control of each and every element connected to Fire Alarm System and Networks.

- The software should have a capacity of 62,500 points or point lists.

- Should be able to store 5,00,000 event logs.

- Quad Monitor supports. Should support multiple active windows such as putting alarm list window in one monitor and the graphic window in another monitor.

- Should be able to customize alarm & messages.

- Pan & Zoom features within a graphic screen for rapid & convenient selection.

- Multiple password option should be available in the software.

- Should operate on Windows 7 32-bit Operating system.

- The proposed software should be from the same manufacture of fire alarm system & should be UL & FM approved.

Client workstation which shall have the following specifications: -

Processor Intel ® i7 750 2.66 GHz with internal memory of 8 GB (expandable to 16 GB) RAM, 2 TB HDD. Operating system Windows® 7 Professional 64-bit. Dual or compatible pair of NICs, 1 Gbps. NVIDIA 2 GB dedicated Graphic Card with detachable keyboard and mouse with required operating system CPU Mother Board with 8 Expansion Slots (7 PCI, 2 ISA) and Dual Video Outputs (1 SVGA, 1 DVI)

Two 1 TB Hard Drives (minimum) capacity with real-time, mirror imaging operation and survivability. Should a failure occur on any one hard drive, the workstation operation shall immediately transfer to the alternate mirror drive without loss of operation and a trouble shall be reported on the Graphical Workstation until the failure mode has been cleared.

24”-inch high-resolution color LCD monitors

DVD Read/ Write

4GB RAM (minimum)

4 available USB Ports, 1 Dedicated for Security Dongle

Two Ethernet Ports to support Remote Clients over Ethernet

[Parallel Port] [Serial Port] [USB Port] for Event Printer

[Parallel Port] [Serial Port] [USB Port] [Ethernet Port] for Graphics and Reports Printer

[UPS Secondary Standby Power Supply, UL Listed for Fire Alarm use]

Pre-programmed functions

Field editor for graphics representations with ability to Import and Export graphic files to AutoCAD

Capability to interface to Legacy 2120 Multiplex Systems.

A fully functional Network Node communicating on the network. Capability to interface with up to seven (7) Network Loops.

The graphical workstation shall be capable of the following operations:

Dynamic pan-and-zoom operation, systems that require multiple graphic screens for each zoom-in/ zoom-out view are not acceptable.

Ability to create predefined zoom levels for rapid zoom into predefined areas within a graphic screen.

Ability to automatically jump to a graphic screen or a predefined zoom level within a screen for each device upon an abnormal status change.

Dual Screen operation with floatable/ dock able windows allowing one screen to display a text-based list of event activity and an alternate screen to display graphical maps simultaneously Information displayed for Point Status, Control, Alarm Lists, Historical Logs, and Reports shall be capable of being sorted by individual categories of information, e.g., Number, Time, Date, Event, Detail, Status, etc.

Ability to assign operator preferences on a per operator basis. The selectable operator preferences shall be:

Font Size: Small or Large

Toolbar Size: Small or Large

User Interface Theme: MS Office 2010

Menu Bar and Toolbar Options: Show/ Hide Menu bar, Show/ Hide Toolbar.

Graphic files shall be capable of being modified in the graphical workstation editor or exported back to AutoCAD file formats where files can be edited in AutoCAD and re-imported for system changes and upgrades.

It shall be possible to import a custom site-specific system banner bitmap used to display a corporate logo or other user preferred system banner background.

It shall be possible to import a custom site-specific main screen bitmap used to display a corporate logo, facility photograph and layout, or other user preferred main screen background image.

The graphical workstation shall have an option for a configurable inactivity timer that automatically logs out inactive users based on a pre-defined inactivity time limit. When no user is logged in, the graphical workstation shall provide view access to system activity. Login to the system shall be required for access to additional control operations.

The Graphical Workstation shall operate by receiving system events and displaying specified graphic representations of the building(s), and system devices. Individual system events shall include a description of the building or area associated with each point in the workstation's views and reports.

The workstation monitor shall be [touch sensitive] [mouse operated] and serve as the interactive interface between the operator and the network system. From the touch screen or mouse, the operator shall be able to perform the following tasks:

Silence signals

Acknowledge all alarm supervisory and trouble events and return to normal conditions.

Log operator notes associated with individual event activity

Select a command link from a graphic screen to call-up an associated webpage, web-camera, or web-link.

Reset system

Display list menus

Select the individual message screens

Perform manual operation of system(s) control points

Enable points into Test Mode to allow testing of selective devices without nuisance interruptions to the workstation operator.

Test Mode events shall be recorded in the background to the workstation’s historical logs

Test mode historical log events shall be flagged with a Test Mode Indicator for easy identification.

Request the "HELP" menu

Perform operator login/ logout

Generate reports that can be printed or saved as an electronic text file. Reports shall include Historical Log, Analog Device Status Report, Analog Device Service Report, AMZ Calibration Report, and Active List Report.

Connect (Set Host) to other nodes

Perform graphic editing functions

Set the system time and date

The unit shall be equipped with at least seven (7) levels of password-protected access.

Remote Ethernet Client Support: The Graphical Workstation server shall be capable of supporting up to 10 Simultaneous Remote Client Connections over Ethernet (maximum of 5 supervised or 10 unsupervised simultaneous client connections, total combined simultaneous client connections not to exceed 10). When the maximum simultaneous client connections have been reached a notice shall be communicated to any additional client connection attempts indicating the connection capacity limit has been reached.

Remote Clients shall be configurable for "Restricted Feature" view only or for "Protected Feature" full control operation.

A minimum 3 Mb/s connection speed shall be provided to Remote Clients

Logins/ Logouts at Remote Clients shall be logged in the Historical Log. Supervised Clients shall be specified by client name.

The Graphical Workstation server shall be capable of supporting both Agency Listed Fire Alarm Ethernet LAN Applications and Supplemental Annunciation over the Customer's Ethernet LAN/ WAN. Where a Fire Alarm Ethernet LAN is specified, only Agency Listed Ethernet hardware shall be installed.

DACR Support. For fire alarm control panels that are not network compatible or may be to remote for a network connection, the Graphical Workstation shall be capable of, and agency listed for, communication with Digital Alarm Communicating Receiver (DACR) via an RS-232 port. Remote fire alarm panels equipped with DACTs shall communicate their local event status to the DACR using dial-up telephone connections/ TCP/ IP protocol/ Wireless communications. The DACR shall forward the individual panel status to the Graphical Workstation for information processing and history logging.

DACR Events. The Graphical Workstation shall handle DACR points as though they were network points. Graphics shall be capable of being displayed on point status changes. Point status changes shall be easily acknowledged locally on the Graphical Workstation. Remote panels need to be Acknowledged, Silenced, or Reset at the panel. Point events shall be entered into the Graphical Workstation history log. The history log shall have a 500,000-event storage capacity minimum.

Supported DACR/ DACT Formats: The Graphical Workstation DACR interface shall support standard reporting formats including SIA, BFSK, 4/2, and ADEMCO CID (Contact ID® format). A CID account shall be configurable on the Graphical Workstation to be either panel event reporting or individual point reporting. The other formats provide panel event reporting only.

Public Points: The Graphical Workstation shall be capable of assigning DACR points as public points to the fire alarm network for monitoring by other network nodes if required.

DACR Status Tracking by the Graphical Workstation: The DACR connection to the Graphical Workstation shall be supervised with the following trouble conditions tracked by the Graphical Workstation:

Communications Loss (between DACR and Graphical Workstation)

Initialization Failed (the Graphical Workstation to DACR connection did not successfully establish)

Unknown DACR Message (the DACR sent a message that was not understood by the Graphical Workstation)

Unknown DACR Account (the account information received does not correlate to a Graphical Workstation point)

Supervision of DACTs: The Graphical Workstation shall be programmed to expect and log periodic supervisory transmissions from the DACTs via the DACR. Failure to receive a supervisory transmission shall cause a trouble event on the Graphical Workstation.

Event Restoration: When the Graphical Workstation receives an event restoration from the DACR, it shall restore that point's status.

Custom Reports: The operator shall be able to create up to 8 user-defined historical log reports. Each custom report shall be capable of being filtered by an individual DACR account.

Graphical Workstation Operating Modes:

When no alarms or troubles are present, the workstation monitor shall display a graphics screen menu used to access other graphic screens. Each screen shall also display current time and date, system status, and present operator name and access level.

Upon activation of any alarm and on request by the operator, the workstation monitor shall display the [floor plan] [coverage zone] [active list] for the device in alarm. of the floor in alarm with all devices shown. The device in alarm shall flash until acknowledged. The device in alarm shall then become steady until cleared.

If a second alarm is registered prior to the first being cleared, the second shall be identified by flashing, pending alarm indication. Touching the pending alarm area shall transfer the display to the second alarm point graphic screen. All subsequent alarms shall be displayed as indicated above. Alternately, the graphical workstation shall be configurable to automatically jump to the graphic screen for the device in alarm. If the auto jump operation is selected and the point in alarm is not associated with a graphic screen, the application shall jump to the active alarm list.

The Graphical Workstation shall cause a "Trouble" condition on all other Network Nodes to indicate an off-line condition.

The Graphical Workstation shall have the capacity to annunciate 50,000 network point and/or point lists.

Historical event logs shall maintain up to 500,000 system events.

Built-in diagnostics shall provide graphical views of the network topology and status. Network communication breaks or inactive nodes shall be clearly indicated as a guide in returning the system to normal.

Individual point access shall display "real-time" analog sensor point information.

The Graphical Workstation shall have the following editing functions:

Message Editor-System shall have the capability of on-site adding, changing, deleting or assigning of message screens.

List Editor - System shall have the capability of on-site editing of customer user lists.

Graphics Editor - System shall have the capability of on-site editing of graphics screens. Graphics editor shall have the capability of changing background graphics and adding or deleting point symbols. Capacity to create and edit up to 25,000 Graphic Screens.

Graphic Annunciator - Led Type

Annunciator Unit, zoned system: Provide an LED-indicating light located on the floor plan for each zone.

Mark zone boundaries on the annunciator floor plan.

Annunciator Unit, addressable system: Provide an LED-indicating light located on the floor plan for each device indicating the type of device and floor on which a signal was actuated.

Provide individual LED indicators for each alarm and supervisory device or zone and a LED to indicate system trouble. Additional LEDs indicate normal power and emergency power modes for the system. A toggle or push-button switch tests the LEDs mounted on the unit. The test switch does not require key operation.

Enclosure: Finish to match Fire Alarm Control Units. The locking cover/ display assembly is hinged on the left. Key and lock shall be common to all secured fire alarm system enclosures.

System Printer

General: Provide a dot-matrix type, listed and labeled as an integral part of the fire alarm system.

Emergency Power Supply

General: Components include battery, charger, and an automatic transfer switch.

Battery: Sealed lead-acid or nickel cadmium type. Provide sufficient capacity to operate the complete alarm system in normal or supervisory (non-alarm) mode for a period of [4][24][48][60][90] hours. Following this period of operation on battery power, the battery shall have sufficient capacity to operate all components of the system, including all alarm notification devices in alarm mode for a period of [5][10][15] minutes.

Addressable Manual Pull Stations

- Description: Addressable single- or double-action type, red LEXAN, with molded, raised-letter operating instructions of contrasting color. Station will mechanically latch upon operation and remain so until manually reset by opening with a key common with the control units.

- Protective Shield: Where required, as indicated on the drawings, provide a tamperproof, clear LEXAN shield and red frame that easily fits over manual pull stations. When shield is lifted to gain access to the station, a battery powered piercing warning horn shall be activated. The horn shall be silenced by lowering and realigning the shield. The horn shall provide 85dB at 10 feet and shall be powered by a 9 VDC battery.

- Manual Pull Station shall be addressable and shall sit on the detection loop of the FACP and shall communicate to the FACP to report its status.

- Manual Pull Station shall be able to generate a manual fire alarm.

- Manual Pull Station shall have an operating temperature range of 0°C to 50°C and humidity range up to 90% RH non-condensing.

- Manual Pull Station shall have manual DIP switch addressing method that does not require any special tool from manufacturer and commissioning activity for replacing the Manual Pull Station in case it goes faulty.

- Manual Pull Station shall be UL and ULC listed, and FM approved.

Addressable Optical Electric Smoke Sensors with Base

General:

Comply with UL 268, "Smoke Detectors for Fire Protective Signaling Systems." Include the following features:

Factory Nameplate: Serial number and type identification.

Operating Voltage: 24 VDC, nominal.

Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore normal operation.

Plug-In Arrangement: Sensor and associated electronic components are mounted in a module that connects to a fixed base with a twist-locking plug connection. Base shall provide break-off plastic tab that can be removed to engage the head/base locking mechanism. No special tools shall be required to remove head once it has been locked. Removal of the detector head shall interrupt the supervisory circuit of the fire alarm detection loop and cause a trouble signal at the control unit.

Each sensor base shall contain an LED that will flash each time it is scanned by the Control Unit (once every 4 seconds). In alarm condition, the sensor base LED shall be on steady.

Each sensor base shall contain a magnetically actuated test switch to provide for easy alarm testing at the sensor location.

Photoelectric Smoke Detector shall offer multiple selectable sensitivity levels from 0.5% Obs/ ft to 3.0% Obs/ ft in order to customize the sensitivity settings.

Optical Smoke Detector shall have automatic drift compensation or environmental compensation capability for different contamination level of different areas in order to counter nuisance alarm.

Optical Smoke detector shall have selectable bases with Response Indicator, Isolator, Sounder, Relay and CO detection capability as an option so that the best fit solution is selected depending on the requirement.

Optical Smoke detector shall have manual DIP switch addressing method that does not require any special tool from manufacturer and commissioning activity for replacing the detector in case the detector goes faulty.

Optical Smoke Detector shall have an operating temperature range of -6°C to 50°C and humidity range up to 90% RH non-condensing.

Optical Smoke Detector shall be UL & ULC listed, and FM approved.

Each sensor shall be scanned by the Control Unit for its type of identification to prevent inadvertent substitution of another sensor type. Upon detection of a "wrong device", the control unit shall operate with the installed device at the default alarm settings for that sensor; 2.5% obscuration for photoelectric sensor but shall indicate a "Wrong Device" trouble condition.

The sensor's electronics shall be immune from nuisance alarms caused by EMI and RFI.

Detector shall be able to monitor or supervise the EMI of environment and report to the main panel.

Sensors include a communication transmitter and receiver in the mounting base having a unique identification and capability for status reporting to the FACP. Sensor address shall be located in base to eliminate false addressing when replacing sensors.

Removal of the sensor head for cleaning shall not require the setting of addresses.

Addressable Bases: Relay output, sounder and isolator bases shall be supported alternatives to the standard base.

Addressable Duct Smoke Sensor:

Photoelectric type, with sampling tube of design and dimensions as recommended by the manufacturer for the specific duct size and installation conditions where applied. Sensor includes relay as required for fan shutdown.

Environmental compensation, programmable sensitivity settings, status testing, and monitoring of sensor dirt accumulation for the duct smoke sensor shall be provided by the FACP.

The Duct Housing shall provide a supervised relay driver circuit for driving up to 15 relays with a single "Form C" contact rated at 7A@ 28VDC or 10A@ 120VAC. This auxiliary relay output shall be fully programmable. Relay shall be mounted within 3 feet of HVAC control circuit.

Duct Housing shall provide a relay control trouble indicator Yellow LED.

Duct Housing shall have a transparent cover to monitor for the presence of smoke. Cover shall secure to housing by means of four (4) captive fastening screws.

Duct Housing shall provide two (2) Test Ports for measuring airflow and for testing. These ports will allow aerosol injection in order to test the activation of the duct smoke sensor.

Duct Housing shall provide a magnetic test area and red sensor status LED.

For maintenance purposes, it shall be possible to clean the duct housing sampling tubes by accessing them through the duct housing front cover.

Each duct smoke sensor shall have a Remote Test Station with an alarm LED and test switch.

Where indicated provide NEMA 4X weatherproof duct housing enclosure that shall provide for the circulation of conditioned air around the internally mounted addressable duct sensor housing to maintain the sensor housing at its rated temperature range. The housing shall be UL Listed to Standard 268A.

Addressable Photo Thermal Smoke Sensors with Base

General:

Comply with UL 268, "Smoke Detectors for Fire Protective Signaling Systems." Include the following features:

Factory Nameplate: Serial number and type identification.

Operating Voltage: 24 VDC, nominal.

Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore normal operation.

Plug-In Arrangement: Sensor and associated electronic components are mounted in a module that connects to a fixed base with a twist-locking plug connection. Base shall provide break-off plastic tab that can be removed to engage the head/ base locking mechanism. No special tools shall be required to remove the head once it has been locked. Removal of the detector head shall interrupt the supervisory circuit of the fire alarm detection loop and cause a trouble signal at the control unit.

Heat Detector shall have both Rate of Rise Temperature operation and Fixed Temperature operation freely configurable as per requirement of site.

Heat Detector shall have two selectable rate of temperature rise thresholds of 8°C per minute & 11°C per minute (or close to this value not deviating by more than 1°C) selectable from the FACP.

Heat Detector shall have two fixed temperature alarm thresholds of 57°C and 68°C (or close to this value not deviating by more than 1°C) configurable from the FACP.

Heat Detector shall have selectable bases with Response Indicator, Isolator, Sounder, Relay and CO detection capability as an option so that the best fit solution is selected depending on the requirement.

Heat Detector shall have manual DIP switch addressing method that does not require any special tool from manufacturer and commissioning activity for replacing the detector in case the detector goes faulty.

Heat Detector shall have an operating temperature range of 0°C to 50°C and humidity range up to 90% RH non-condensing.

Heat Detector shall be UL & ULC listed, and FM approved.

Each sensor base shall contain a magnetically actuated test switch to provide for easy alarm testing at the sensor location.

True alarm photo sensing technology selectable sensitivity from 0.2% to 3.7%/ ft obscuration or as per EN54 standard.

Each sensor shall be scanned by the Control Unit for its type of identification to prevent inadvertent substitution of another sensor type. Upon detection of a "wrong device", the control unit shall operate with the installed device at the default alarm settings for that sensor; 2.5% but shall indicate a "Wrong Device" trouble condition.

The sensor's electronics shall be immune from nuisance alarms caused by EMI and RFI. The detector shall be able to monitor or supervise the EMI of environment and report to the main panel.

Sensors include a communication transmitter and receiver in the mounting base having a unique identification and capability for status reporting to the FACP. Sensor address shall be located in base to eliminate false addressing when replacing sensors.

Removal of the sensor head for cleaning shall not require the setting of addresses.

Addressable Bases: Relay output, sounder and isolator bases shall be supported alternatives to the standard base.

Addressable Heat Sensors with Base

Thermal Sensor: Combination fixed-temperature and rate-of-rise unit with plug-in base and alarm indication lamp; 54 deg C or 69 deg C fixed-temperature setting except as indicated.

Thermal sensor shall be of epoxy encapsulated electronic design. It shall be thermistor-based, rate-compensated, self-restoring and shall not be affected by thermal lag.

Sensor fixed temperature sensing shall be independent of rate-of-rise sensing and programmable to operate at 54 deg C or 69 deg C. Sensor rate-of-rise temperature detection shall be selectable at the FACP for either 8.3-deg C per minute.

Sensors shall have the capability to be programmed as a utility monitoring device to monitor for temperature extremes in the range from 32-deg F to 155-deg F.

Very Early Smoke Detection System

Provide an air sampling smoke detection system (Very Early Smoke Detection Apparatus - VESDA) for each area shown in the Contract Documents. Provide a [Laser Focus air sampling smoke detection system for areas up to 2500 sq. ft.] [Laser COMPACT air sampling smoke detection system for areas up to 8000 sq. ft.] [Laser PLUS air sampling smoke detection system for areas up to 20000 sq. ft.] or Micro Sensor, Pro Sense and Top Sense work on high power LED in accordance with manufacturer's recommendations.

The air sampling smoke detection system shall consist of highly sensitive smoke detectors with aspirating fans, air sampling pipe network, filters, networked controllers and a high-level interface to the building Fire Alarm System, as required.

The air sampling detectors shall provide a nominal obscuration level range from 0.0015 to 6%/ ft., adjustable through the system operator control interface.

Multiple VESDA systems serving protected areas shall be integrated via closed loop VESDA net 2-wire communications and a high-level RS-232 interface with the building Fire Alarm System. The system will provide access to all VESDA features and functions through the Fire Alarm Control Panel operator's interface.

The Fire Alarm System supplier shall coordinate the installation and testing of the VESDA system, in accordance with applicable codes and the Contract Documents. Provide complete VESDA system design, installation, interface, and programming to include the following:

Smoke Detector Assembly: The smoke detector, filter, and aspirating fan shall be housed in a Detector Control Assembly Enclosure and arranged in such a way that air is drawn from the protected area through the filter and detector by the aspirating fan.

The Detector Control Assembly shall house the programmable intelligent controller, which will support air flow/ detector supervision, automatic and manual sensitivity adjustment, time delay and remote reset functions. Laser COMPACT detector shall communicate with the FACP via IDNet channel.

The system shall provide 3 field-selectable levels of alarm status: Alert Level 1 (.04% obscuration/ ft.), pre-Alarm Level 2 (1.06 % obscuration/ft.) and Alarm Level 3 (2.6% obscuration/ ft.). Actual sensitivity levels will be determined in the field and programmed during system commissioning. Alarm Levels 1 and 2 will initiate a Supervisory Condition on the Fire Alarm System, and Alarm Level 3 will initiate the building-wide evacuation sequence as described elsewhere in the Contract Documents.

Air Sampling Pipe Network: Shall consist of a ¾ inch nominal inside diameter pipe arranged to provide optimal efficiency and air transport times which shall not exceed 60 seconds from the furthest point on the network. Sampling points shall be separated at intervals specified in NFPA 72; not more than 30 feet and typically in the range of 13-to-26-foot intervals along the path of the piping network. Air sampling calculations shall be provided from a registered VESDA sampling pipe aspiration modeling program ASPIRE rev. 1.8 or later.

High Level Interface: Where VESDA net is used, provide interface module integral to the Fire Alarm Control Panel with connection to the High-Level Interface Module and installed in the VESDA net equipment rack assembly.

Addressable Very Early Aspiration Smoke Detection System

Provide a Very Early Smoke Detection (Laser COMPACT/ Micro Sense) air sampling smoke detection system for areas up to 400 sq.mtr. The air sampling smoke detection system shall consist of highly sensitive smoke detectors with aspirating fans, air sampling pipe network, filters, networked controllers and a high-level interface to the building Fire Alarm System, as required.

The air sampling detectors shall provide a nominal obscuration level range from 0.016% to 4.08%/ ft., adjustable through the system operator control interface.

The Fire Alarm System supplier shall coordinate the installation and testing of the VESDA system, in accordance with applicable codes and the Contract Documents. Provide complete VESDA system design, installation, interface, and programming to include the following: Smoke Detector Assembly: The smoke detector, filter, and aspirating fan shall be housed in a Detector Control Assembly Enclosure and arranged in such a way that air is drawn from the protected area through the filter and detector by the aspirating fan.

The Detector Control Assembly shall house the programmable intelligent controller, which will support air flow/ detector supervision, automatic and manual sensitivity adjustment, time delay and remote reset functions. Laser COMPACT/ Micro Sense detector shall communicate with the FACP via addressable loop protocol.

The system shall provide 3 field-selectable levels of alarm status: Alert Level 1 (.04% obscuration/ ft.), pre-Alarm Level 2 (1.06 % obscuration/ ft.) and Alarm Level 3 (2.6% obscuration/ ft.) or as per EN54 standard. Actual sensitivity levels will be determined in the field and programmed during system commissioning. Alarm Levels 1 and 2 will initiate a Supervisory Condition on the Fire Alarm System, and Alarm Level 3 will initiate the building-wide evacuation sequence as described elsewhere in the Contract Documents.

Addressable Aspiration Smoke Detection System (Normal Sensitivity)

Aspiration unit with pre-installed addressable sensor is designed to cover areas up to 1800 to 3600 square feet based on the number of sensors. This coverage would be carried out by using single or two pipe networks, active air sampling techniques combined with addressable smoke sensing technology available with single/ dual inlet detection system.

Provides remote sensor location for difficult service areas—up to 50 ft. with flexible tubing or 82 ft. with rigid pipe.

Aspiration unit provides airflow monitoring circuitry and an aspiration system that is configurable. The airflow level is displayed on a ten-element bar graph with adjustments for flow sensitivity and high/ low flow thresholds and can be adjustable air speed settings from the Aspiration unit for easy setup.

Individual smoke sensitivity selection and Aspiration smoke sensor have Sensitivity Range - 0.5% to 3.0%/ foot obscuration.

Optional water trap with drain prevents nuisance alarms associated with condensation buildup.

Directly sit at addressable loop without using any interface module and communicate all information to panel and Ability to display and print detailed sensor information Smoke sensitivity in percent per foot and in easy-to-understand terms.

Beam Detector

Beam detector shall have selectable bases with Response Indicator, Isolator, Sounder, Relay and CO detection capability as an option so that the best fit solution is selected depending on the requirement.

Beam detector shall have manual DIP switch addressing method that does not require any special tool from manufacturer and commissioning activity for replacing the detector in case the detector goes faulty.

Beam Detector shall have an operating temperature range of -6°C to 50°C and humidity range up to 90% RH non-condensing.

Beam detector shall have range from 10Mtr – 50Mtr.

Beam Detector shall be UL & ULC listed, and FM approved.

UL listed to Standard 268

A single unit houses both an infrared transmitter and receiver. The transmitter signal is received by a receiver where the internal microprocessor analyzes it for the presence of smoke. An alarm condition is determined when the selected sensitivity level is reached.

Operation at either 12 VDC or 24 VDC

The beam detector shall feature automatic gain control which will compensate for gradual signal deterioration from dirt accumulation on the lenses.

Programmable Control Module

Control Module shall be addressable and shall sit on the detection loop of the FACP and shall communicate to the FACP to report its status.

Addressable Control Module for switching ON of smoke extraction fans/ Pressurisation Fans etc. and switching off AHU' s, capable of being addressed electronically.

Control Module shall have an operating temperature range of 0°C to 50°C and humidity range up to 90% RH non-condensing.

Control Module shall have manual DIP switch addressing method that does not require any special tool from manufacturer and commissioning activity for replacing the control module in case it goes faulty.

Control Module shall be UL and ULC listed, and FM approved.

Programmable Monitor Module

Monitor Module shall be addressable and shall sit on the detection loop of the FACP and shall communicate to the FACP to report its status.

Monitor Module shall supervise flow switches/ interface with any third-party equipment capable of being addressed electronically.

Monitor Module shall be configurable to report supervisory signal and alarm signal.

Monitor Module shall have an operating temperature range of 0°C to 50°C and humidity range up to 90% RH non-condensing.

Monitor Module shall have manual DIP switch addressing method that does not require any special tool from manufacturer and commissioning activity for replacing the monitor module in case it goes faulty.

Monitor Module shall be UL and ULC listed, and FM approved.

Addressable Fault Isolator Module

Fault Isolators shall be addressable and shall sit on the detection loop of the FACP and shall communicate to the FACP to report its status.

Fault Isolators shall be dual port, bidirectional communication isolator so that it isolates the short-circuited wire of any side (left side or right side).

Fault Isolators shall be compatible to isolation from the FACP for the field diagnostic purposes.

Fault Isolator shall power up in isolated mode and shall be directed by FACP to connect the detection loop segment. It shall connect the detection loop segment only if the segment is short-circuited free and acceptable else shall remain in isolated mode to impart short-circuit survivability and tolerance to the remaining detection loop.

Fault Isolator shall be fully monitored and addressable by FACP. It shall report its status to the FACP and shall be controlled from FACP.

Fault Isolator shall have an operating temperature range of 0°C to 50°C and humidity range up to 90% RH non-condensing.

Fault Isolator shall have manual DIP switch addressing method that does not require any special tool from manufacturer and commissioning activity for replacing the fault isolator in case it goes faulty.

Fault Isolator shall be UL and ULC listed, and FM approved.

Magnetic Door Holders

Description: Units shall be listed to UL 228. Units are equipped for wall or floor mounting as indicated and are complete with matching door plate. Unit shall operate from a 120VAC, a 24VAC or a 24VDC source, and develop a minimum of 25 lbs. holding force.

Material and Finish: Match door hardware.

Addressable Alarm Notification Appliances

Addressable Notification Appliances:

The Contractor shall furnish and install Addressable Notification Appliances and accessories to operate compatible signaling line circuits (SLC).

Addressable Notification appliance operation shall provide power, supervision and separate control of horns and strobes over a single pair of wires or Horns and Strobes shall be addressable loop powered. The controlling channel (SLC) digitally communicates with each appliance and receives a response to verify the appliance's presence on the channel. The channel provides a digital command to control appliance operation. SLC channel wiring shall be unshielded twisted pair (UTP), with a capacitance rating of less than 60pf/ ft and a minimum 3 twists (turns) per foot.

Class B (Style 4) notification appliances shall be wired without requiring traditional in/ out wiring methods; addressable "T" Tapping shall be permitted. Up to 63 appliances can be supported on a single channel.

Each Addressable notification appliance shall contain an electronic module and a selectable address setting to allow it to occupy a unique location on the channel. This on-board module shall also allow the channel to perform appliance diagnostics that assist with installation and subsequent test operations. A visible LED on each appliance shall provide verification of communications and shall flash with the appliances address setting when locally requested using a magnetic test tool.

Addressable Controller: Addressable Controller shall supervise Channel (SLC) wiring, communicate with and control addressable notification appliances. It shall be possible to program the High/ Lo setting of the audible (horn) appliances by channel from the addressable controller.

Horn: Addressable horn shall be listed to UL 464. Horn appliances shall have a High/ Lo Setting, programmable by channel from the addressable controller or by appliance from the host FACP. The horn shall have a minimum sound pressure level of 83 or 89 dBA @ 24VDC. The horn shall mount directly to a standard single gang, double gang or 4" square electrical box, without the use of special adapter or trim rings. Appliances shall be wired with UTP conductors, having a minimum of 3 twists per foot.

Visible/ Only: Addressable strobe shall be listed to UL 1971. The V/O shall consist of a xenon flash tube and associated lens/ reflector system. The V/O enclosure shall mount directly to standard single gang, double gang or 4" square electrical box, without the use of special adapters or trim rings. Appliances shall be wired with UTP conductors, having a minimum of 3 twists per foot. V/O appliances shall be provided with different minimum flash intensities of >2Cd. Provide a label inside the strobe lens to indicate the listed candela rating of the specific Visible/ Only appliance.

Audible/ Visible: Addressable combination Audible/ Visible (A/V) Notification Appliances shall be listed to UL 1971 and UL 464. The strobe light shall consist of a xenon flash tube and associated lens/ reflector system. Provide a label inside the strobe lens to indicate the listed candela rating of the specific strobe. The horn shall have a minimum sound pressure level of 90 dBA@ 24VDC. The audible/ visible enclosure shall mount directly to standard single gang, double gang or 4" square electrical box, without the use of special adapters or trim rings. Appliances shall be wired with UTP conductors, having a minimum of 3 twists per foot. The appliance shall be capable of two-wire synchronization with one of the following options:

Synchronized Strobe with Horn on steady.

Synchronized Strobe with Temporal Code Pattern on Horn.

Synchronized Strobe with March Time cadence on Horn.

Synchronized Strobe firing to NAC sync signal with Horn silenced.

Speaker/ Visible: Combination Speaker/ Visible (S/V) units combine the speaker and visible functions into a common housing. Addressable functionality controls visible operation, while the speaker operates on a 25VRMS or 70.7VRMS NAC.

Twisted/ shielded wire is required for speaker connections on a standard 25VRMS or 70.7VRMS NAC and UTP conductors, having a minimum of 3 twists per foot is required for addressable strobe connections.

The following taps are available: 1.5W, 3W, and 6.0W. At the 6.0W tap, the speaker has minimum UL rated/ EN54 rated sound pressure level of 88dBA at 10 feet.

The S/V shall have a frequency response of 400 to 4000 Hz for Fire Alarm and 125 to 12kHz for general signaling.

The S/V installs directly to a 4" square, 1 ½" deep electrical box with 1 ½" extension.

Isolator Module: Isolator module provides short circuit isolation for addressable notification appliance SLC wiring. Isolator shall be listed to UL 864. The Isolator shall mount directly to a minimum 2 1/8" deep, standard 4" square electrical box, without the use of special adapter or trim rings. Power and communications shall be supplied by the Addressable Controller channel SLC; dual port design shall accept communications and power from either port or shall automatically isolate one port from the other when a short circuit occurs. The following functionality shall be included in the Isolator module:

Report faults to the host FACP.

On-board Yellow LED provides module status.

After the wiring fault is repaired, the Isolator modules shall test the lines and automatically restore the connection.

Addressable Textual Notification Appliance: Textual Notification Appliance is to operate on a compatible Signaling Line Circuit (SLC) and is to provide a high visibility, multi-color LED text message display.

Textual Notification Appliance shall be Listed to UL 1638 Visual Signaling Appliances.

Appliance shall be capable of up to thirty-two (32) pre-programmed message selections that can be activated in response to pre-defined emergency situations or linked to specific system point status conditions.

Textual Notification Appliance shall be capable of displaying dual or single line emergency instructions.

Instructions can show as static, flashing, or scrolling with a variety of appearance/ transition options.

Instructions shall be capable of displaying using multi-colors to emphasize instructions content.

Textual Notification Appliance shall be capable of providing non-emergency information during non-emergency conditions. Emergency conditions will override non-emergency message/ instructions and display emergency instructions.

Textual Notification Appliance shall be capable of scrolling instructions of at least 854 characters in length.

Textual Notification Appliance shall be viewable from a distance of 100 feet.

Textual Notification Appliance shall be powered by a listed fire alarm power supply providing 24VDC with battery back-up.

Textual Notification Appliance shall be capable of wall or ceiling mounting options.

Standard Conventional Alarm Notification Appliances

Horn: Piezoelectric type horn shall be listed to UL 464. The horn shall have a minimum sound pressure level of 85 dBA@ 24VDC. The horn shall mount directly to a standard single gang, double gang or 4" square electrical box, without the use of special adapter or trim rings.

Visible/ Only: Strobe shall be listed to UL 1971. The V/O shall consist of a xenon flash tube and associated lens/ reflector system. The V/O enclosure shall mount directly to standard single gang, double gang or 4" square electrical box, without the use of special adapters or trim rings. V/O appliances shall be provided with different minimum flash intensities of 15cd, 75cd and 110cd. Provide a label inside the strobe lens to indicate the listed candela rating of the specific Visible/ Only appliance.

Audible/ Visible: Combination Audible/ Visible (A/V) Notification Appliances shall be listed to UL 1971 and UL 464. The strobe light shall consist of a xenon flash tube and associated lens/ reflector system. Provide a label inside the strobe lens to indicate the listed candela rating of the specific strobe. The horn shall have a minimum sound pressure level of 85 dBA@ 24VDC. The audible/ visible enclosure shall mount directly to standard single gang, double gang or 4" square electrical box, without the use of special adapters or trim rings.

Speaker/ Visible: Combination Speaker/ Visible (S/V) units combine the speaker and visible functions into a common housing. The S/V shall be listed to UL 1971 and UL 1480 standard.

Twisted/ shielded wire is required for speaker connections on a standard 25VRMS or 70.7VRMS NAC.

The following taps are available: 1.50W, 3.0W and 6.0W. At the 6.0W tap, the speaker has minimum UL54rated sound pressure level of 88dBA at 10 feet.

The S/V shall have a frequency response of 400 to 4000 Hz for Fire Alarm and 125 to 12kHz for General Signaling.

The S/V installs directly to a 4" square, 1 ½" deep electrical box with 1 ½" extension.

Speaker: Speaker notification appliances shall be listed to UL 1480/ EN54.

The speaker shall operate on a standard 25VRMS or 70.7VRMS NAC using twisted/ shielded wire.

The following taps are available: 1.50W, 3.0W and 6.0W. At the 6.0W tap, the speaker has minimum UL54 rated sound pressure level of 88dBA at 10 feet.

The S/V shall have a frequency response of 400 to 4000 Hz for Fire Alarm and 125 to 12kHz for general signaling.

The S/V installs directly to a 4" square, 1 ½" deep electrical box with 1 ½" extension.

Notification Appliance Circuit provides synchronization of strobes at a rate of 1Hz and operates horns with [an On Steady] [a Temporal Code Pattern] [a March Time cadence] operation. The circuit shall provide the capability to silence the audible signals, while the strobes continue to flash, over a single pair of wires. The capability to synchronize multiple notification appliance circuits shall be provided.

Accessories: The LSTK Contractor shall furnish any necessary accessories.

Network System Integrator (NSI)

The Network System Integrator shall provide Agency Listed integration capable of communicating the status information from multiple brands and/or vintages of control panels onto the fire alarm network for reporting at a central command center location and at other network nodes (panels).

Protocol communication interfaces for systems integration that require ongoing protocol development necessary to maintain compatibility and agency listings with new versions of software releases shall not be substituted.

The Network System Integrator shall receive primary and secondary power from an alternate source.

The Network System Integrator shall provide 8 isolated voltage monitor inputs for status communication onto the network.

Inputs shall be rated to monitor voltages from 10 to 33 VDC.

Inputs shall be compatible with direct switched or reverse polarity circuits.

The Network System Integrator shall provide 8 dry contact relay outputs for interface to monitored equipment.

Each output shall be configurable for normally open or normally closed contact operation.

Output contacts shall be rated for 1A @ 24VDC/ 25VAC or 0.5A @ 70VAC

7 relay outputs shall be programmable

1 relay output shall be normally energized and dedicated for trouble operation.

The Network System Integrator shall be capable of maintaining Fire Alarm Network communications with other network nodes (panels) when the monitored interface panel is powered down for service.

Active Repeater Panel

Repeater panel should be active type where control switches should be available for system acknowledge, Alarm silence & system reset.

LCD test should be possible.

Active Repeater panel should be UL and ULC listed, and FM approved.

Addressable Hooter with Strobe

Hooter with strobe should be true addressable system.

Hooter with Strobe unit shall have both audible and visual output units housed within the same device. The audible output shall be multi-tone horn output up to 90DB and strobe output shall have selectable intensity of 15, 30, 75 and 110 candela.

Strobe unit shall have a flash rate of 1Hz synchronized throughout the Fire Alarm Network.

Hooter with Strobe unit shall be connected to the NAC of FACP and it shall be fully monitored by FACP.

Hooter with Strobe unit shall report its status with configured parameters of each unit (hooter and strobe) to FACP.

Hooter with Strobe unit shall support individual field testing in “Silent Mode” and “Non-Silent Mode” (full operational mode).

If asked for, it shall be possible for FDA system to generate, print and e-mail the diagnostic report of notification devices with tested and verified parameters.

Hooter with Strobe unit shall be controlled independently on the same 2-Core NAC as per programmed activation and deactivation criteria or from the FACP. Audible (hooter) and Visible (strobe) outputs shall be independently configurable from FACP for its activation and deactivation criteria as required.

In absence of any specific mention of activation and deactivation criteria, the hooter shall stop at “Alarm Acknowledge” or “Alarm Silence” and the strobe shall stop at “System Reset” or “Panel Reset”. This requirement shall not be deviated from unless otherwise stated cause-n-effect configuration or unless a formal written approval is taken from the design consultant.

It shall be possible to poll each and every hooter with strobe unit from the HMI/ Display/ Operator Console at FACP, isolate and include in the circuit (NAC), activate and deactivate, view the voltage received by it from the HMI/ Display/ Operator Console at the FACP & Network Repeater.

It shall be ensured that the last notification device at respective NAC receives at least 20Vdc (or 3 V above the min operating voltage) to ensure the desired performance. There shall be a provision to verify the same either from FACP or a hand-held testing device.

Hooter with Strobe unit shall support individual performance check by a hand-held testing tool during in “Silent-Mode” or “Sound-Mode” to facilitate performance check during normal working hour.

Hooter cum Strobe shall have an operating temperature range of 0°C to 50°C and humidity range up to 90% RH non-condensing.

Hooter with Strobe unit shall be UL and ULC listed, and FM approved.

Fire Fighter Telephone Station

Fire Fighter Telephone Station shall be complete with Telephone Jack, Handset and required accessories.

Operator at Command Centre shall be able to connect or disconnect to multiple simultaneous fire fighters/ callers from the field with unambiguous addressability/ identification of each caller.

It shall be possible for the operator at main command centre to set up a conference call among fire fighters trying to speak to the operator at the main command centre.

The Fire Fighter Telephone Station shall be UL listed.

PUBLIC ANOUCEMENT AND EVACUATION SYSTEM

Introduction

The Networked Digital Public address system is configured for broadcasting information and emergency announcements to the public. A public address system which will be provided should be IP networked system. The public address system is designed and installed to be suitable for use during emergency conditions accordingly.

General Description

Public Address system provided should be completely networkable over IP. The system will distribute background music and pre-recorded messages through the graphical user interface and live announcements from the call stations. The recessed ceiling-type loudspeakers are to be used mostly providing PA coverage in where the false ceiling is present. For areas without false ceiling, wall mount loudspeakers will be installed to provide PA coverage. The PA system should provide an announcing console at the Main Centre Control Room. The system architecture should be daisy chain in nature complying with the following standards.

Applicable standards

BS 5839-8 – Code practice for the design, installation, and servicing of voice alarm system.

IEC 60849 – Sound systems for emergency purposes

BS EN 54 -16 Voice control indicating equipment and alarms Emergency according to

EN60849/ EN54-16/ ISO 7240-16 EN-54 - For entire Public Address system.

The system should allow an undistorted speech reproduction of 85dB SPL at listening level. The system should also provide uniform coverage within +/‐5dB for the entire area.

Function Summary

Call Station Function

Call Station: The operator/ user can make an announcement to any zone or any combination of zones of that station via the call station. The type of announcements that are allowed from the call station are: Live announcements.

Pre-recorded announcements

Background music

Pre-recorded emergency announcements

Emergency Announcements: The pre-recorded announcements can be initiated by the fire alarm signal that is sent from the fire alarm system.

The operator can make an announcement to any combination of zones in the system.

Pre-recorded Announcements: The pre-recorded announcement can be activated from the pre-defined keys at the call station and scheduled to be played at specific times.

Fault Indication: The failure of the PA equipment will be notified to the call station in the system; and the fault will also be presented in the configuration/ diagnostic and logging PC located in the communications equipment room in the building.

The PA system should be capable of integration with BMS system seamlessly. It provides digital audio signal processing and transmission of audio signals via a simple IP network system. The audio transmission in the system is in digital form except for the 100V line from the power amplifiers to the loudspeakers.

The PA system is comprised of the following basic elements:

Network controller

Power Amplifiers

PA call stations

Network cables

Loudspeakers

Background Music Source

The PA system elements are connected by the daisy chain principle. The interconnection between the system units is achieved by using either plastic or glass optical fibre cable. The system cabling can be implemented in ring network whereby a single failure on the network cable will not affect the functioning of the system.

The equipment for the PA system, i.e., network controller, power amplifiers, and PA call stations, have built-in audio processing facilities, the audio processing is done in the digital domain.

The distribution of PA cables is configured to ensure that the failure of an amplifier, a cable or a speaker does not render the PA system inoperative or result in the total loss of PA facility in any part of any zone.

Equipment Specification

Network controller

The control unit is the heart of the public address system. The unit shall be capable of routing minimum 28 audio channels, delivering power to the system, fault reporting and controlling of the system. This unit can work either as stand-alone mode or with a PC connected to it. It should have at least the following functionalities:

There shall be 8 control inputs, which should be freely programmable.

The network controller shall have analog audio line outputs for fire alarm signals, music sources etc. The network controller shall have the capability to handle at least 100 levels of priorities and 200 zones, 30 call stations or MMI (Man Machine Interface)

The network controller shall monitor the status of all zones in the system and the last 200 status change and fault events should be logged.

Attention and alarm tone definitions shall be stored in the network controller or recalled from an external storage device through control ports. These tones can be accessed by any call stations or control inputs for announcement broadcast or alarm broadcast.

At least 4 pre-recorded messages should be played simultaneously.

The network control unit shall have extensive audio processing possibilities for audio inputs and audio outputs. Parametric equalization, limiter, and gain can be adjusted with the configuration software.

The network controller shall monitor the status of all equipment including the status of the microphone capsule of a call station and report any fault.

The network controller should have hot standby auto switchover facility to redundant controller.

The system shall be able to make emergency calls (all calls) even if the network controller has failed.

The controller should have a 16x2 front panel LCD display and rotary control, through which debugging of faults will be possible.

The network controller is EN-54 certified and complies with the safety and emergency standards according to EN54-16 and EN60849 standards.

Technical Specification

| Power Source | 115/230 VAC ±10%, 50/60 Hz |
| --- | --- |
| Battery Power | 48V DC |
| Supply |  |
| Power | 14W with no load, 150W with maximum |
| consumption | load |
| Audio inputs | 28 channels |
| Control Inputs | 8 |
| Control Outputs | 8 |
| Line Outputs | 4 |
| Operating | -50C to +550C |
| Temperature |  |
| Frequency | 20 Hz to 20 kHz (-3 dB) |
| response |  |
| Event Logs | 200 |

Power amplifiers

The main function of the power amplifier is the amplification of audio signals for the loudspeakers. It shall be possible to select the output voltage between 100V and 70V by changing jumpers.

It should have at least the following functionalities:

The amplifier should have DSP built in for Equalization, delay settings etc. The noise dependent Automatic Volume Control (AVC) circuitry should be built in. Each amplifier should have min two channels for AVC function.

The amplifier monitoring and changeover facility shall be incorporated with the power amplifier. The changeover relays shall be integrated with the standby unit. In case of failure of any working amplifier, the standby amplifier shall automatically come in the circuit.

The amplifier should have rotary or push control for selection of system enquiry mode and Headphone volume along with LCD display.

The amplifier should have built-in line and loudspeaker supervision, automatic volume control, automatic ventilation temperature control, auto change over to DC power supply.

The power amplifier should be capable of monitoring the speaker lines (zones) connected to it through pilot tone supervision.

Separate amplifiers or separate channels of amplifiers for every zone.

The network controller is EN-54 certified and complies with the safety and emergency standards according to EN54-16 and EN60849 standards.

Power amplifier technical specifications are as follows:

| Main’s supply |  | 115/ 230VAC 10% at 50 - 60 Hz |
| --- | --- | --- |
| Type of Amplifiers |  | Class D |
| Indication & Controls |  | 854-character LCD display for status display |
|  |  | Rotary/ push control for selection of system |
|  |  | enquiry mode. |
| Output power |  | 1x1500W, 1x500W, 2x250W, 4x125W, 8x60W as |
|  |  | required. |
| Outputs |  | Selectable 100V, 70V. |
| Audio Inputs |  | Mono, balanced |
| Control Inputs |  | 8 |
| Control Outputs |  | 1 or 2 or 4 or 8 depending on the amplifier type. |
| Frequency response |  | 60 Hz to 20 kHz (-3 dB). |
| Frequency | Response | Line: -3dB at 20Hz and 20KHz |
| (Audio inputs) |  |  |
|  |  | Mic: -3dB at 100Hz to 16KHz |
| Total harmonic distortion |  | <0.3% (1 kHz) at 50% of rated power |
| Cross talk |  | -70 dB (1 kHz) nominal (only multichannel). |
| Signal to noise ratio |  | >85 dB with pilot tone off |
| Battery Power Supply |  | 48V |
| Safety and Emergency |  | According to EN 60849 and EN 54-16 |

Loudspeaker

Metal grille Ceiling Speaker 6 Watts

Compact 6 W ceiling speakers with fire dome for indoor areas. The product should have wide opening angle, with perforated metal grill of approved color and with the following specifications: The speakers are EN-54 certified and complies with the safety and emergency standards according to EN54 and EN60849 standards.

Technical Specifications:

| Rated Power | 6W |
| --- | --- |
| Sound pressure level at 6 W | 90 dB |
| Field Selectable Tapings at | 1.5W, 3W, 6W |
| Frequency Range (-10dB) | 90Hz -20 KHz |
| Opening Angle at 1 kHz/4 kHz (-6 dB) | 180°/ 50° |
| Rated Voltage | 100V/ 70 |
| Diameter | 216 mm (8.5 in) |
| Maximum depth | 90 mm (3.54 in) |
| Weight | 1.3 kg (2.86 lb) |
| Colour | off-white (RAL 9010) |
| Safety compliance | EN60065 |

Passive Line Array Loudspeaker

The loudspeaker should have excellent directivity and high-power output, can handle medium and large indoor environments.

Technical Specifications:

|  | Power output | 60W RMS output, with multi tap for |  |
| --- | --- | --- | --- |
|  |  | 60/30/15W |  |
|  | Frequency response | Better or equal to 190Hz to 18kHz |  |
|  | SPL level at 30W/1W (at 1KHz | 110 dB/ 92 dB (SPL) |  |
|  | ,1m) |  |  |
|  | Opening angle at (1kHz/4 kHz |  |  |
|  | 6dB) |  |  |
|  | Horizontal | 210 deg/ 132 deg |  |
|  | Vertical | 50 deg/ 22 deg |  |
|  | It shall have minimum 12 nos. of 2”drivers |  |  |
|  | Safety | acc. to EN 60065 and CE |  |
|  | Emergency | acc. to EN 54 24/ EN 60849 |  |
|  | Water and dust protection | acc. to IEC 60529, IP 32 |  |
|  | Dimensions (H x W x D) | 1200x80x90mm (47.24x3.15x3.54 in) |  |
|  | Weight | 6,4 kg (14,1 lb) |  |
|  | Color | Light gray (matches RAL 9022) |  |

Hemi-directional Loudspeaker

The speaker is suitable for large area and high-ceiling applications. Innovative loudspeaker which projects consistent and high-quality sound, ensuring superb reproduction of background music and high speech intelligibility for paging or emergency calls. The opening angle and high sound pressure level allows it to be suitable for indoor high ceiling areas like warehouses, transport and exhibition halls, mega stores and swimming pools.

Certifications and Approvals

Safety acc. to EN 60065

Emergency acc. to BS 5839 8/ EN 60849

Self-extinguishing acc. to UL- 94 V 0

Flame retardant acc. to UL 94 5VA

Water and dust protection acc. to EN 60529 IP 42

Chlorine resistant acc. to IEC 60068/2 60

| Power Output | 150W |
| --- | --- |
| Sound pressure level at 100 W /1 W (1 kHz, 110/ 90dB 1m) | 100W (100-50-25W) |
| Effective frequency range (10 dB) | 60 Hz to 20 kHz |
| Rated voltage | 100 V, 70 V and 28.3 V |
| Opening angle at 1 kHz/ 4 kHz (6 dB) | 175º/ 96º (horizontal) 180º/ 137º (vertical) |
| Rated impedance | 100ohm, 50 ohm and 8 ohm |
| Connector | Ceramic screw terminal |
| Dimensions (dia. x H) | 800 x 425 mm (31.50 x 16.74 in) |
| Weight | 27 kg (59.52 lb) |
| Color baffle | White (RAL 9010) |
| Color grille | Silver (RAL 9006) |
| Color top cover | Silver (RAL 9023) |
| Material | ABS TSG |

Mechanical impact acc. to EN 50102 IK 07

Technical Specifications are as follows:

Call Station

Remote Call Station

Remote call station is to be used for car calling purpose and other applications with following functionalities:

Connects to call station interface via CAT-6A cable.

Up to 1 km from digital public address optical network.

Uses standard keypads for extension.

Built-in limiter.

Powered via CAT-6A and/or local power supply and complete supervision. Supervision of the microphone capsule should be present.

The network controller is EN-54 certified and complies with the safety and emergency standards according to EN54-16 and EN60849 standards.

Technical Specifications:

| External | power |  | 18 to 56 VDC |  |
| --- | --- | --- | --- | --- |
| supply |  |  |  |  |
| Power |  |  | 2.9 W at 48 V without keypads |  |
| consumption |  |  |  |  |
| Microphone |  |  |  |  |
| Nominal | acoustic |  | 75 to 90 dB SPL |  |
| input level |  |  |  |  |
| S/N |  |  | >60 dB at 85 dB SPL |  |
| Frequency |  |  | 340 Hz to 14 kHz (-3 dB) |  |
| response |  |  |  |  |
| Loudspeaker |  |  |  |  |
| S/N |  |  | 80 dB at max. |  |
| Sound | pressure |  | 85 dB (SPL) at 0.5 m and 1 kHz |  |
| level |  |  |  |  |
| Headset Connector |  |  | 3.5 mm jack |  |

Call station keypad

Safety covers to prevent accidental activation of the keys should be available as an option.

The keypad gets its power from the call station it is connected to. The call station keypad shall have following features:

Controls and indicators

- Eight function keys

- Eight two-color LEDs Interconnections

- Two serial data and power connections

PC Call station

The PC call stations will be used for the Controller’s call stations in the main Control Room.

The PC Call station is used for making live speech or pre-record announcements to any zone or a group of zones or to execute any pre-defined actions. The PC Call Station is comprised of a high quality Praesideo microphone on a gooseneck, user-friendly operation PC software and a PC with a 19” Touch screen LCD monitor. The PC Call station software provides the user with a powerful and easy-to-use tool that brings all aspects of announcements to a single point control.

The on-screen configuration sections allow the user to enter the properties of zones of individual zone such as entering the name of a zone/ group, pre-defined input/ output relay actions and selected attention/ alarm tones or pre-recorded messages. After configuration, the user can operate the system via the operation key layout section.

IP Audio Interface

The VOIP interface is a universal, IP‑based audio device supporting VoIP and Audio over IP applications. It is an ideal solution for bridging audio and contact closures over long-distance LAN and WAN networks, The unit has analog audio inputs and outputs for easy interfacing with optional pilot‑tone supervision for emergency sound purposes. One audio input can be switched to microphone sensitivity with built‑in microphone supervision. Also, the control inputs offer cable and connection supervision. Control inputs and outputs can be used to set up an audio connection to start a remote call, but also to pass remote fault events to the system controller.

Audio Setting

Multiple audio formats are supported: single channel, full duplex 16-bit PCM or G.711 for very low latency, and two channel send or receive MP3 for high quality audio with ‑various sample rates and compression.

Network Interfaces

The unit interfaces to 10 and 100 Mbit Ethernet networks and announces its IP address that was given by a DHCP server. It can also search the network for a free IP address or can be given a static IP address. A second Ethernet connection is available to support network redundancy. An RS 232 interface is built in to communicate additional serial data over the IP network.

Connector	Dual RJ45, DTE-pinout

Standard	802.3i/ 802.3u

Speed	10/ 100 Mbps, auto-negotiation

Flow	Full/ half-duplex, auto-negotiation

Protocol	TCP/ IP, UDP, RTP, IGMP, DHCP, SNMP

Cable and Wiring

Network Cable

The network cable is a special cable with 2 plastic fibres for communication and 2 copper cores for the power supply. The cable is supplied with network connectors fitted. This cable can be used to connect the network controller to power amplifiers, call station etc.

| Wire | Copper, stranded 1 mm2 |
| --- | --- |
| Resistance | <0.018 ohm/m |
| Optical Fiber | PMMA, 1 mm |
| Numeric aperture | 0.5 |
| Attenuation | <0.17 dB/m at 650 nm |
| Bending loss | <0.5 dB (r=20 mm, 90°) JIS C6861 |

LIGHT GUIDE INTERCONNECT UNIT (LIU)

TECHNICAL FEATURES:

Rack Mount Type LIU fully populated with required modules, connectors, etc. shall be supplied and installed as required. It shall be installed for terminating the OFC cables. It shall provide minimum bending radius and the splice trays shall function as a splice cover for pigtail splicing. It shall be of complete aluminium fully powder coated. Cable glands shall be provided for secure anchoring the incoming cables.

Rubber grommets shall be provided at the cable entry point for tight sealing. The splice tray shall also be of aluminium powder coated with splice holder. Cable and spools shall be of flame-retardant type.

OFC CONNECTORS

It shall be single mode SC/ LC type with push-pull mechanism, fully in compliance, with latest industry standards. It shall be possible for selection of wide range of ferrule hole diameter selection.

OFC ADAPTORS

It shall be suitable for single mode SC/ LC type fiber cable connectors which shall be fully in compliance with latest industry standard. It shall be with snap/ latch mechanism.

OFC PATCH CORDS

It shall be suitable for single mode SC type fiber cable connectors with plastic moulded plug type connectors. Standard 2.5 mm ceramic ferrules shall be used. It shall be compact and easy to connect.

PATCH CORDS

- Push & pull design with latch.

- Shall be wired straight through.

- Bend relief compliant boots to ensure proper Cat 6 performance.

PATCH PANEL

- Conform to EIA standards.

- Have Port identification numbers on both front and rear of the panel.

NETWORK SWITCHES

a. All network equipment offered shall be of One OEM.

b. Ethernet Network shall consist of Layer 3 Core Switches in redundancy in Equipment room.

c. Ethernet Network shall consist of Layer 3 Core Switches/ Layer 2 Distribution/ Zone Switches in field interconnected in such a manner that there is no single point of failure.

d. Layer 3 Switches & POE enabled 24 port Layer 2 Switches shall be supplied fully populated with required modules, 24 port Jack Panel, 6/9U Rack, LIU, suitable power socket, SM Optic Fibre, Cat-6 patch cords, connectors etc. as required complete as per specifications.

e. The LSTK Contractor shall get the Network design approved by AAI before execution.

LAYER 3, 12 SFP FIBER PORT, CORE SWITCH HAVING FOLLOWING CONFIGURATION:

TECHNICAL SPECIFICATIONS:

A. PERFORMANCE

a. 12 Fibre ports (populated with at least 6 Nos. of 1Gbps SM Fibre Modules).

b. Dual Redundant CPU in Active-Active mode or a set of two nos. of Switches in Active-Active redundancy mode.

c. It should be stackable with minimum 12 Gbps of Stacking Bandwidth.

d. IPv6 fully compliant and ready from day one.

e. Shall have minimum 8K MAC Address

f. Minimum 06 active VLANs

g. Shall have minimum 24 Gbps or more Switching Fabric h. Shall have minimum 17 Mpps forwarding rate

B. RELIABILITY

a. Shall have hot swappable modules and fan modules

TECHNICAL FEATURES:

C. IEEE STANDARDS

a. IEEE 802.1Q VLAN and VLAN tagging

b. IEEE 802.3ad Link aggregation control protocol-Ether Channel c. IEEE 802.1p Priority Tagging or equivalent d. IEEE 802.1D Spanning Tree Protocol

e. IEEE 802.1w Rapid Reconfiguration of Spanning Tree f. IEEE 802.1s Multiple VLAN Instances of Spanning Tree g. IEEE 802.1x User Authentication

h. IEEE 802.3 Ethernet and IEEE 802.3ae

10 Gigabit Ethernet

D. SECURITY

a. 802.1x user authentication and accounting

b. Support for Dynamic and Guest VLANs

c. Shall provide Local and Remote Port Mirroring

d. (Network Device Protection Profile/ Evaluation Assurance Level) NDPP/ EAL2 compliant or equivalent

E. QUALITY OF SERVICE

a. Shall have sophisticated QoS and Traffic Management

- Shall have Per-port QoS configuration

- Shall have strict priority queuing

- Shall have IP differentiated service code point (DSCP) and IP precedence

- Shall support Congestion Avoidance feature

- Routing: Advanced routing protocol like RIPing, OSPFv3, VRRPv3 from Day 1 and support for BGPv4

F. MANAGEMENT

a. Shall have GUI and CLI support

b. Shall have out of band Ethernet management port and/or console management port c. Shall have SSH, SNMPv3 and NTP support

LAYER 2, 24 PORT POE SWITCH TECHNICAL SPECIFICATIONS:

A. PORT DENSITY

a. 24 Nos. 10/100/1000 Base-T PoE Ports with minimum 2 Nos. of additional SFP based Uplink ports and one console port

b. Uplink ports populated with 2 nos. of single mode fibre ports connecting to core switches.

- Support non-blocking architecture

- Support multicasting for traffic.

- Support stacking.

- IP v6 fully compliant and ready from day one.

B. POWER OVER ETHERNET

- Power over Ethernet to all 24 nos. 10/100/1000 Base-T ports

- Support for up to 24 nos. Class 3 Powered devices at 15.4 watts

C. PERFORMANCE

- 128 MB RAM or more

- 64 or more VLAN

- 1,024 or more MAC address

- Forwarding rate 12 Mpps or more

D. INTERFACE SUPPORT

- 10/100-TX RJ-45

- 10/100/1000TX RJ-45

- 1000-SX, 1000-LX/LH, 1000-ZX SFP slot

- RJ45 or RS232 DB9 pin or male port or console port

E. MANAGEMENT

a. Shall have GUI and CLI support

b. Shall have out of band management console serial port.

c. Shall have SSHv2, SNMPv3 and NTP support

F. QUALITY OF SERVICES

a. Shall have sophisticated QoSand Traffic Management

- Shall have Per-port QoS configuration

- DiffServ Precedence for 8 queues per port

- Shall have IP Differentiated Service Code Point (DSCP) and IP precedence

G. SECURITY

- 802.1x user authentication and accounting

- Support for Dynamic and Guest VLANs

- DHCP Snooping, IP Source Guard, BPDU Protection and

- STP Root Guard

- Shall provide Local and Remote Port Mirroring

- RADIUS Accounting or equivalent

H. GENERAL STANDARDS

a. IEEE 802.1Q VLAN and VLAN tagging

b. IEEE 802.3ad Link aggregation control protocol

c. IEEE 802.1p Priority Tagging or equivalent

d. IEEE 802.1D Spanning Tree Protocol

e. IEEE 802.1w Rapid Reconfiguration of Spanning Tree f. IEEE 802.1s Multiple VLAN Instances of Spanning Tree g. IEEE 802.1x User Authentication

Wiring

LPCB certified 2c x 1.5 sq.mm Fire Survival/ Resistance Armoured cable (600/ 1000V) with class-2 Copper conductor having halogen free ceramified silicon rubber insulation as per BS EN 50363 and low smoke zero halogen (LSZH) inner & outer sheath. Should comply to EN 61034-2 & EN 60754-1. LPCB-FPC certificate to be submitted. The cables should meet fire performance circuit integrity test as per BS EN 50200: PH-120. Outer sheath should be in red colour with Anti-rodent & LSZH properties, 950°C rating for three hours for fire alarm system. (with fixing arrangement & termination.)

The cable manufacturer should provide factory production control certificate related to the manufacturing of fire-resistant wires & cables from LPCB/ BRE-Global.”