## Summary
Civil Works for "Construction of LNMIIT Mess Building"
ABSTRACT
S.No. | ITEM | AMOUNT
1 | CIVIL AND FINISHING WORK
2 | PLUMBING WORK
3 | ELECTRICAL WORK
4 | C.C. ROAD
5 | FAS & PA SYT.
6 | FIRE HYDRANT SYSTEM
7 | BIOMETRIC SYSTEM
8 | LAN & WIFI
9 | CCTV
TOTAL
0

## CIVIL & FINISHING ABSTRACT
CIVIL WORK FOR "CONSTRUCTION OF LNMIIT MESS BUILDING "
BOQ CIVIL WORKS -MESS BUILDING
S. No. | ITEM DESCRIPTION | QUANTITY | UNIT | RATE | AMOUNT
GENERAL NOTES
i | All taxes to be mentioned clearly
ii | All samples to be made/fabricated/purchased by contractor and to be approved by client/ consultant before procurement and execution.
iii | For any civil / dismantling works, contractor to prepare and submit final proposal after carrying out structural audit along with structural consultants (appointed directly by contractor), NDT, and certification prior to initiation of work in contractors scope.
iv | Bidder to inspect site before submitting final offer to client as after bid submissions, all items would be assumed in client / contractor scope whether mentioned or not required for physical execution of works
v | All mock ups & samples to be done by contractor free of cost.
vi | Civil Works (Under direct supervision and direction of Client's Engineer-In-Charge) - Cost to be all inclusive incl. disposal to municipal place where directed by EIC, scaffolding, labour, material, tools, tackles etc. - Cost to also include for any charges related to structural audit, verification, testing, vetting etc. at site
vii | All debris generated by contractor must be dumped and carted away from the site to approved dumping ground as per local statutory norms.
viii | Electrical & water supply to be in contractor's scope
ix | Stores & arrangement of temporary toilet at site to be in contractor's scope & no open fire permitted at site
x | Unless otherwise specified, The rate shall include cost of labour, material, wastages, tools & plants, necessary scaffolding, stacking and safety of materials, necessary accessories, loading and unloading charges, transportation and all other incidental charges, etc., complete as per drawings and specifications, of any depth, any shape, with leads and lifts, all works at all levels and as per the directions of the Engineer In charge, Complete in all manners to the satisfaction of the Client.
xi | For ambiguity with specifications, drawings if any, description in bill of quantities shall have precedence as regards rate quoted. The offer is for item wise contract and measurements.
xii | Quantities may be increase or decrease as per site condition or requirement on execution stage.
xiii | Contractor to follow all requirements for safety , NGT norms also and local guideline as per client
xiv | Ceiling heights mentioned in drawings are indicative / minimum allowed and to be maximised to the extent feasible as per site conditions after all MEP and other engineering Services have been coordinated and installed.
xv | General contractor to ensure that they adhere strictly to working hours specified by building management & ensure their teams are provided best in class tools & safety gear etc complete
XVI | Esclation free contract
Part I | EARTH WORK & SITE DEVELOPMENT
01.01 | Earth Work In Excavation in all types of soil & soft rock include all trenches, such as earth, marine clay, marshy land, running sand, garbage, slush, murum, rock boulders with pick axe & shovel or mechanical means like hydraulic excavator (by manual or mechanical means) etc. as directed by Engineer-In-Charge. The rate includes cost of labour, plants, machinery, power, fuel, consumables, equipments, pumping out water, setting out the works in profile, providing shoring and strutting for protecting the sides of foundation where required. The rates includes of Disposal or dumping of surplus excavated earth (after Refilling ) of all kinds of soil up to disposal point as directed by Engineer-in-charge with in the premises. Work shall be completed in all respect as per the technical specifications and as per the directions of the Engineer in charge. all safety parameters shall be ensured as required by the relevant IS Codes, Industry Practice or as instructed by representative to take care of the Owners property. -- Measurements shall be done on PCC Dimensions Only. lead and liftup to 2 KM .
01.01.01 | In depth from Existing Ground level to 3 m level or more | 5945.925 | Cum |  | 0
01.02 | Back filling / Filling available earth including removing heaped / stacked earth at required locations, in layers not exceeding 200 mm thickness, including mixing, spreading, levelling watering and consolidating each layer with power / hand roller of required capacity to obtain required 98% maximum dry density. all complete and as directed. well compacted after sprinkling required quantity of water. Measurement shall be taken only after compaction Rate shall include for loading, unloading, transportation, hire and fuel charges for tools and plants employed and other incidental charges etc. complete work in all respect as per direction of EIC.Filling with selected available earth including transportation for all leads, and upto any height cost of soil, royalty, loading, unloading, carriage to dumping spot and all incidentals complete (Net consolidated area fill volume will be computed from the initial and final levels. Volume in slopes, embankments etc. will be computed applying appropriate formula). lead and liftup to 2 KM . | 4435.2786 | Cum |  | 0
01.03 | Providing and laying dry rubble soling thick as required hand set in regular lines, interstices being filled in with small pieces of stones, hard murrum etc. thoroughly rammed, consolidated and watered complete as directed and specified complete as per specification and as per direction of Engineer-in-Charge. | 483.6174 | Cum |  | 0
01.04 | Supply and filling with good earth brought from outside (excluding rock and black cotton soil) such as moorum or other type of earth as approved by the Client/Consultant, in trenches, sides of the foundations, plinth & plot etc, in layers not exceeding 300 mm. in depth, including breaking the clods, watering to optimum moisture content, ramming and compacting by mechanical means to achieve 98% proctor density using mechanical vibrator, including freight, transportation, loading, unloading, screening, passes etc. all complete as instruction & directions of the Engineer-in-charge (Compacted volume /measurement of fill shall be paid for under this item). The rates shall include for all leads and lifts including transporting using mechanical / manual means within the plot area. The rate shall be inclusive of required water for compaction, to achieve required compaction density, same shall be under contractor's scope. [Compaction shall be carried out for each layer of 300mm and proctor density shall be executed at 1000 Sq.m Per 3 No of Sample or more] 1. Royalty shall be submitted for the total quantity of earth filling. 2. The contractor has to carry out initial survey before starting the filling work and final survey after completing the plot filling work and has to submit both the survey sheets to client and consultant. 3. Contractor shall have to submit each layer compaction test report to Consultant / Client and after approval further layer of filling can be start & Mesaurment will be of compacted area | 1000 | Cum
01.05 | Providing & Laying Anti Termite Treatment (Pre-constructional chemical treatment measures) along the internal & external vertical faces of the columns, plinth beams, foundation and all structure surface of the filling below flooring bed as per the specified procedure conforming to IS 6315 (Part-2) 2001 and other relevant approved specification duly using Chlorpyriphos/ Lindane emulsifiable concentrate 20% with 1% concentration @ 7.5 Liters/ sqm of the vertical surface & @ 5.0 Liters/ sqm of the horizontal surface of the substructure to a depth of 500 mm around columns & 300 mm deep around plinth beams, filling area including excavation channel along the wall & rodding etc. & cost & conveyance of all materials to the site, cost of labour for spraying, rodding etc. complete for finished item of work as per the approval of the Engineer-in-Charge. ( For payment plinth area to be measured) Work to be done only by the specified Application vendor. | 1758 | Sqm |  | 0
01.06 | Random Rubble stone masonry with hard stone in superstructure above plinth level and upto five level & foundation above 30cm thick walls in : Cement Mortar 1:4 ( 1-Cement : 4-Sand) | 144.4275 | cum |  | 0
Part II | PLAIN / REINFORCED CEMENT CONCRETE WORK
(Quoted Rates shall be for full Heights & Depths)
02.01 | Providing & laying in position plain cement concrete of specified grade in raft, bases of column footing, Brick walls footing, base of floor, lintels, vanity counter, band etc as screed over areas to make up levels or to form slopes, laid to required levels and grade at all locations, consolidated finished fair and cured including side forms as required complete of specified grade including the cost of cantering and shuttering and complete work in all respect as per direction of EIC.
02.01.01 | 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) | 343.7882 | Cum |  | 0
02.02 | Providing and laying damp proof course 50mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) including mixing of water proofing compound as directed by the project-in-charge | 285.5385 | Sqm |  | 0
02.03 | Providing and laying in position ready mixed or design mix cement concrete M-25 grade ( Make: UltraTech RMC, and Nuvoco) cement concrete for reinforced cement concrete work, using cement content as per approved design mix for all elements, all level all height, including manufacturing, transporting, pumping, laying, vibrating and curing, excluding the cost of centering, shuttering and finishing, including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability for all works up to all levels, as per direction of the Engineering- charge. Also add waterproofing agent for footing , lift pit & Water Tank. including cost of making shear keys and provision of construction / contraction / control joints in various locations, laid, consolidated and cured. Item to include all structural items like base raft, ramp, column, wall, footings, equipment foundations, fins, mullions, beams, lintels, pergola, chajja, facia, parapet, railing, slab trenches, drains and sumps etc. This item to also include the concrete requiring waterproofing like water tanks, retaining walls, base raft, etc.
02.03.01 | Footings / Lift pit / grade slab / wall foundation etc. | 499.6905 | Cum |  | 0
02.03.02 | Columns of any shape including circular | 255.861 | Cum |  | 0
02.03.03 | Plinth beam, beams/lintel | 1317.791 | Cum |  | 0
02.03.04 | Suspended floors, roofs, landings, chajja, shelves, counters | 907.125 | Cum |  | 0
02.03.05 | Sloping waist slab of stair flights | 12.4425 | Cum |  | 0
02.04 | Providing and fixing in position to correct line, level and plumb, plane, form-work and shuttering & de-shuttering in all shapes all height of shuttering ply or any other approved materials of rigid design, faces based with approved form oil to prevent adhesion of concrete to forms etc. to give finish (as per detailed specification) for slabs, beams, columns, chhajjas, foundations, machine foundations including splayed edges, notching, allowance for overlap, nosing angles, battens, strutting, casing, bolting, nailing etc., racking or circular cutting etc. including leaving necessary recesses, opening for pockets, inserts etc. including providing and fixing all staging scaffolding struts, braces, supports, props etc. including caring, striking and removing from site etc. all complete. The rate should also include supply of all materials, labor, and T&P etc. and complete the work in all respect as per direction of EIC.
Approved Shuttering Ply 12 mm thik for footing , Beam, Slab And 18 mm Thik Ply for Column Shuttering (Make: Century & Kitply) and Scafolding shuttering above 3 mtr centering for structural concrete work (Plain and reinforced) in locations called for including strutting, propping, bracing, bolting, wedging, casing, striking, removal etc. complete. Props shall consist of well designed steel pipes adequately braced using X- and K-bracings (wooden ballies as props shall not be permitted). The item to include centering and shuttering at all heights and levels.
Allow for forming grooves, drips throats, chamfers, cut-outs, openings etc. where called for and for dressing with approved shuttering oil (Make: Sika, Fosroc, Addage, Eastern Petroleum, and SCL) to prevent adhesion. Unexposed concrete surfaces subsequently left untreated (in the condition obtained on removal of form work) It shall not constitute exposed concrete work and shall be measured under this item only. .
02.04.01 | For wall and column footings | 897.807 | Sqm |  | 0
02.04.02 | For suspended floor, shelves, landings | 6058.5 | Sqm |  | 0
02.04.03 | For beams, lintels etc. | 9622.868 | Sqm |  | 0
02.04.04 | Staircase waist slab | 111.5725 | Sqm |  | 0
02.04.05 | For columns | 2669.208 | Sqm |  | 0
02.05 | Providing, fabricating & placing in position of M.S. reinforcement/ H.Y.S.D tested bars Fe 550 D CRS as per IS 1786-2008, make Tata, JSPL, SAIL .(Yield strength 5500 Kg/sq.cm.) of all dia. in all types of work with proper cover blocks supports chairs, spacers, etc. fixing and binding of reinforcement with 18 SWG black soft annealed wire(make: Tata, JSPL) (binding wire ,Dowels, Chairs, Pins etc.will not be measured and paid as approved by E.I.C.). The rate shall include labor, T&P, cost of binding wire etc. required for proper completion of work including transportation to site straightening, cutting, bending cranking binding welding etc. as per drawing specification and as directed by Engineer-in-charge, only authorise lab shall be consider and paid | 299290.998 | Kg |  | 0
Part III | MASONRY WORKS
Preamble
The rates quoted shall include:
i | Hacking and roughening of concrete or other surfaces in contact with masonry for bondage.
ii | Leaving out dowels from concrete member for anchorage.
iii | Levelling up and preparing tops of wall for damp proof courses, precast units, plinth beams etc.
iv | Holes (cut and formed or left) for fixing, pipes, bolts & inserts & making good including grouting if necessary.
v | Forming chases for edges of concrete floors or other units, for sealing in waterproofing layers etc.
vi | The efflorescence patches appearing on brick work shall be washed with a light solution of HCL or other chemicals to give efflorescence free surface.
vii | Making all projections, recess, Grooves , cornices and elevation features
viii | Necessary curing and protection
ix | Provision for recesses, openings, toothing, curing, raking of joints.
x | Single / multi-stage scaffolding wherever situations warrant such requirements.
xi | The masonry to be with fair face from external side.
xii | Works at all heights and levels. All lead lift, loading, unloading, cartage, handling and storage.
xiii | All lead lift, loading, unloading, cartage, handling and storage.
03.01 | MASONRY WORK : providing and laying brick work using common burnt clay conventional building bricks conforming to IS 1077-1922 having compressive strength not less than 12.5 N/mm2 in any shape and all depth including curing, scaffolding etc. complete as directed by engineer-in-charge. (ii) CM 1:6 (1 Cement : 6 coarse Sand)
| Brick work of thickness 230 mm and above in super structure joints finished, flush raked to 6mm depth including jointing with concrete where required .including providing & placing 230x230 mm Bend 4 nos. 10 mm dia, 8 mm dia rings@150 c/c MS bars reinforcement at directed by the engineer-in-charge, curing , anchoring With rebar Chemical.(hilti ) | 1154.3573 | Cum |  | 0
03.02 | Providing and laying half brick masonry with common burnt clay conventional building bricks conforming to IS 1077-1922 having compressive strength not less than 12.5 N/mm2 at all heights, levels, locations and shapes etc. including curing, scaffolding etc. complete as directed by the engineer-in-charge including providing & placing 2 nos. 8mm dia MS bars reinforcement at every fourth course, curing , anchoring with concrete .(ii)CM 1:4 (1 Cement : 4 coarse Sand) as per specification and drawing or as directed by Project Manager. | 987.4674 | Sqm |  | 0
Part IV | WATER PROOFING TREATMENT
Preamble: Rate shall include
i | The water-proofing treatment shall be carried out through approved specialists in the field and under their direct supervision & strictly as per approved specification.
ii | The treatment shall be guaranteed against leakages / dampness, etc. for the treated areas for a period of 10 years from the date of handing over of the building to owner. The guarantee will have to be given by the Agency directly to the owner on specified format/ stamp paper.
iii | The treated area shall be tested by 48 hours ponding with water to the satisfaction of the Project manager to prove the effectiveness of the treatment.
iv | Treatment of down take pipes and other obstructions.
v | All cutting, dressing, trimming, protection, etc.
vi | Providing concrete fillet at the junction of horizontal and vertical surfaces.
vii | Preparation of surface for water proofing work, insulation and other related treatments.
viii | Work in narrow width, bands, strips and at all locations.
ix | All lead/lift, loading/unloading, cartage, handling etc.
04.01 | Providing and laying water proofing treatment by applying cement slurry mixed with water proofing cement compound consisting of applying : (a) First layer of slurry of cement @ 0.488 kg/SQM mixed with water proofing cement compound @ 0.253 kg/ SQM. This layer will be allowed to air cure for 4 hours. (b) Second layer of slurry of cement @ 0.242 kg/SQM mixed with water proofing cement compound @ 0.126 kg/SQM. This layer will be allowed to air cure for 4 hours followed with water curing for 48 hours.(The rate includes preparation of surface,injection grouts treatment and sealing of all joints, corners, junctions of pipes and masonry with polymer mixed slurry.) as approved specifications of the approved specialist agency including providing 10 years written guarantee against any defect ( For Toilets, balcony, kitchen/ pantry overhead water tank) Make of water proofing compound: CICO, SIKA, fosroc | 2706.15 | Sqm |  | 0
04.02 | Providing and laying integral cement based water proofing treatment including preparation of surface as required for treatment of roofs, terraces etc consisting of following operations: (a) Applying a slurry coat of neat cement using 2.75 kg/sqm of cement admixed with water proofing compound conforming to IS. 2645 and approved by Engineer-in-charge over the RCC slab including adjoining walls up to 300 mm height including cleaning the surface before treatment. Make Dr. Fixit or Pidilite as per EIC. (b) Laying brick bats with mortar using broken bricks/brick bats 25 mm to 115 mm size with 50% of cement mortar 1:5 (1 cement : 5 coarse sand) admixed with water proofing compound conforming to IS : 2645 and approved by Engineering- charge over 20 mm thick layer of cement mortar of mix 1:5 (1 cement :5 coarse sand ) admixed with water proofing compound conforming to IS : 2645 and approved by Engineering- charge to required slope and treating similarly the adjoining walls up to 300 mm height including rounding of junctions of walls and slabs. (c) After two days of proper curing applying a second coat of cement slurry using 2.75 kg/ sqm of cement admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge. (d) Finishing the surface with 20 mm thick joint less cement mortar of mix 1:4 (1 cement :4 coarse sand) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge including laying glass fibre cloth of approved quality in top layer of plaster and finally finishing the surface with trowel with neat cement slurry and making pattern of 300x300 mm square 3 mm deep. (e) The whole terrace so finished shall be flooded with water for a minimum period of two weeks for curing and for final test. “All above operations to be done in order and as directed and specified by the Engineer-in-Charge : With average thickness of 120 mm and minimum thickness at Khurra as 65 mm. complete work in all respect as per direction of EIC. Only plan area shall be measured. Make of water proofing compound: CICO, SIKA, PIDILITE. | 1443 | Sqm |  | 0
04.03 | Providing gola 75mm x 75mm in cement concrete 1:2:4 (4 graded stone aggregate 10mm down gauge) including finishing with plaster 1:3 (1 cement : 3 fine sand) etc . Complete as required. | 168.3 | Rmt |  | 0
04.04 | LIGHT WEIGT FILLING -Filling on floor as applicable shall be of Light weight Polystyrene filling of density less than 20 kg per cum as per direction of EIC. | RO | Cum
Part V | WOOD WORKS
1 | Wood Plastic Composite Door Frames:
| Factory made single extruded WPC (Wood Polymer Composite) solid door/ window/ Cleosetory windows & other Frames/ Chowkhat of minimum size Frame size 50 x 100 mm, comprising of virgin PVC polymer of K value 58-60 (Suspension Grade), calcium carbonate and natural fibers (wood powder/ rice husk/ wheat husk) and non-toxic additives (maximum toxicity index of 12 for 100 gms) fabricated with mitre joints after applying PVC solvent cement and screwed with full body threaded star headed SS screws having minimum frame density of 750 kg/cum, screw withdrawal strength of 2200 N (Face) & 1100 N (Edge), minimum compressive strength of 58 N/mm2, modulus of elasticity 900 N/mm2 and resistance to spread of flame of Class A category with property of being termite/ borer proof, water/ moisture proof and fire retardant and fixed in position with SS dash fasteners of required dia and length complete as per specification and drawing. | 130 | Rmt
2 | Wood Polymer Composite Door shutter
| Factory made 30 mm thick single extruded WPC (Wood Polymer Composite) solid decorative type flush door shutter of required size comprising of virgin polymer of K value 58-60 (Suspension Grade), calcium carbonate and natural fibers (wood powder/ rice husk/wheat husk) and non-toxic additives (maximum toxicity index of 12 for 100 gms) having minimum density of 650 kg/cum and screw withdrawal strength of 1800 N (Face) & 900 N (Edge), minimum compressive strength 50 N/mm2, modulus of elasticity 850 N/mm2 and resistance to spread of flame of Class A category with property of being termite/borer proof, water/moisture proof and fire retardant. WPC to be laminated with PVC foil of minimum 14 microns thick of approved design pasted with hot melt adhesive on both faces of shutter and fixing with stainless steel butt hinges of required size with necessary full body threaded star headed counter sunk S.S screws, all as per specification and drawing. | 50 | Sqm
05.01 | Providing wood work in frames of doors and other frames, sawn and fixed in position with hold fast / dash fasteners including applying coat of wood preservative, polishing / synthetic enamel paint etc. complete as per design and drawing.
05.01.01 | First class African teak wood (Basic price of wood is Rs 1500/- per cuft) | 20 | Cum |  | 0
05.03 | P / F Single Leaf / Double leaf seasoned hardwood Flush Door : (Size: as Drawing) fabricated in 35-40 mm thk.flush door Panel finished 1mm thick laminate (as/sample approved make) on both faces. The laminate has to be fixed with hairline grooves. All the laminate grains to be vertical & spray applied spray applied PU ( ICA, Pidilite make) finished (Seasoned red merantii wood) margin match to laminate shade on exposed edges as per design, and 100mm high 1mm thk. 304 grade SS kick plate wrapped around at bottom of door on both faces to be adhesive bonded and all door hardware including 150mm high SS pull handle, S.S butt hinges , floor mounted D type door stop, open arm door closer, mortise or Cylindrical round handle cum lock or mortise handle with lock , 100mm high 0.5mm thk. 304 grade SS kick plate wrapped around at bottom of door on both faces and behind the door handle of approved makes as per hardware drawing etc & including fire proof paint of Viper/ Acro make on all edges of panel. all complete as per design and drawing. ( The thickness of shutter in all the cases should not be less than 35mm either veneered or laminated finish) (Cost of providing 40 mm beading, door seal to be included in the quoted rate). SS brush hardware only
05.03.01 | 35 m.m. thick shutters | 195.384 | Sqm |  | 0
05.03.02 | Extra For providing Laminate on Any Side of the Door including fevicol or equivalent glue, pasting etc complete 1.0mm Thick. Laminate Both side of the shutters . (Base rate of laminate : INR 650 / Sq. mt.) SS brush hardware only | 390.768 | Sqm |  | 0
05.04 | Providing and fixing Brushed steel hardwares
05.04.01 | Providing and fixing tower bolt (barrel type) with necessary screws etc. complete.
05.04.01A | 250 x 10mm. | 40 | Each |  | 0
05.04.01B | 150 x 10mm | 22 | Each |  | 0
05.04.02 | Providing and fixing brushed steel handles with necessary screws etc. complete.
05.04.02A | 150 mm | 124 | Each |  | 0
05.04.03 | Providing and fixing sliding door bolts
05.04.03A | 300 mm | 70 | Each |  | 0
05.04.03B | 250 mm | 70 | Each |  | 0
05.04.04 | Door stopper | 124 | Each |  | 0
Part VI | FLOOR AND WALL TILES
Preamble:
Rates shall include :
i | All handling and storage, All lead/lift, loading, unloading, cartage, handling etc.
ii | Protection with approved material
iii | To the true line and levels
iv | As per the approved pattern and design
v | Making all projections , recess and aesthetical features
vi | Making necessary cut outs, holes, Fixing all inserts
vii | making necessary cutting for accommodating cp, sanitary(wash basin, sink etc.) etc. and finish such edges as per approved drawing or as instructed by project manager
viii | All riser & tread shall be in single piece, no joint shall be allowed.
ix | Tiles and stone shall be of uniform colour and same batch number
x | Necessary slope shall be maintained .
xi | Silicon shall be applied to all joints with backer rods on external cladding works
xii | The contractor shall be responsible for protection of his works up to handover to Project Manager, protection like laying Bubble sheet/ POP protection sheet/ Synthetic material sheet (Floor Guard) over stone/ tile work where-ever as required. (as directed by Project Manager.)
06.04 | Providing and laying 20mm thick Granite to staircase with 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) and joint to be filled with white cement pigmented slurry to match the shade of granite etc. complete including 0.5mm machine cut edges to be champhered and polished, polishing on stone as per drawing as per EIC.
06.04.01 | Treads of steps including rounding the edges and providing 3 nos. non skid grooves of size 3mm x 3mm per tread. ( Base Rate 220 Sft Without GST) | 123.57 | Sqm |  | 0
06.04.02 | Riser of steps granite ( Base Rate 220 Sft Without GST) | 65.535 | Sqm |  | 0
06.05 | P / L of Matte finish 8-9 mm thk. anti skid Full body Vitrified tiles in Toilet (600X600MM), Kajaria / Somany or approval make, shade as approved by Architect & code using upto 1:4 (1 cement & 4 coarse sand) cement mortar bed below including 100mm high skirting, after that use tiles adhesive for Fixing ( Make:Pidilite (Roff),MYK LATICRETE), with machine cutting as required,with 3 mm spacers & including joints treated with epoxy laticrete grout in approved shade sample to tile ,with water jet cutting as required, in flooring making slope as required etc complete in all respects as per flooring pattern given in the drawing including providing cut-outs wherever necessary as per MEP requirements.
06.05.01 | Anti skid Full body Vitrified tiles Toilet Floor ( Base rate – 1250 INR / Sq. mt. Without GST ) | 164.26 | Sqm |  | 0
P / L of Matte finish 12-15 mm thk. Full body Vitrified tiles In Floor (600X600MM), Kajaria / Somany or approval make, shade as approved by Architect & code using upto 1:4 (1 cement & 4 coarse sand) cement mortar bed below ,after that use tiles adhesive for Fixing ( Make:Pidilite (Roff),MYK LATICRETE), with machine cutting as required,with 3 mm spacers & including joints treated with epoxy laticrete grout in approved shade sample to tile, including 100 mm high skirtingwith water jet cutting as required, in flooring making slope as required etc complete in all respects as per flooring pattern given in the drawing including providing cut-outs wherever necessary as per MEP requirements.
06.05.02 | Vitrified tile ( Base rate – 1450 INR / Sq. mt. Without GST ) | 3500 | Sqm |  | 0
P / F, 9-10 mm thk. Matte finish full body Vitrified wall tiles All Kitchen, Toilet etc. (300mmx450mm) of Kajaria / Somany or approval make, and shade ,including rough cement plaster 1:5 ration of thickness 15-20mm under tile, tile to be fixed on rough plaster using 1:3 ( 1 cement & 3 coarse sand) mortar,after that use tiles adhesive for Fixing ( Make:Pidilite (Roff),MYK LATICRETE), with machine cutting as required,with 3 mm spacers & including joints treated with epoxy laticrete grout in matching color to tile,complete in all respects as per wall cladding pattern given in the detailed dwg. & as per specifications etc complete in all respects including providing cut-outs wherever necessary as per MEP requirements. With SS genesis make corner guard in tile edge . As per EIC.
06.06 | Vitrified tile ( Base rate – 600 INR / Sq. mt. Without GST ) | 1098.81 | Sqm |  | 0
06.07 | Providing and fixing prepolished 20 mm thick Granite slab for the toilet counter & facial laid ,including rough cement plaster 1:5 ration of thickness 15-20mm under tile, tile to be fixed on rough plaster using 1:3 ( 1 cement & 3 coarse sand) mortar,after that use tiles adhesive for Fixing ( Make:Pidilite (Roff),MYK LATICRETE), with machine cutting as required,with 3 mm spacers & including joints treated with epoxy ,complete in all respects as per wall cladding pattern given in the detailed dwg. & as per specifications etc complete in all respects including providing cut-outs wherever necessary as per MEP requirements. With SS genesis make corner guard in tile edge . As per EIC. over approved adhesive inclusive of making and rounding off edges and cutting holes (circular or oval) for wash basin, MS angle to fix bottom stone including rubbing polishin P / F 450-600mm deep toilet counter unit for recessed wash basin as approved, top finished 18-20 mm thick granite of approved shade and make with front fascia, nosing etc to be complete in all respects including providing cut-outs wherever necessary as per MEP requirements (Note : ).
06.07.01 | Counter top/ Facial Dado granite ( Base Rate 220 Sft Without GST) | 370.118 | Sqm |  | 0
P / L of 20 mm the. Polished Granite in flooring, patterns, thresholds and including ramp, as per approved sample, including using 1:4 (1 cement & 4 coarse sand) mortar, with machine cutting as required, joints treated with Altercate make grouting material to match the shade of stone, rate to include diamond polish with over sealer coat of Nano make sealant and skirting etc. complete in all respects as per flooring pattern given in the detailed drawing complete .
06.08 | Providing and fixing prepolished 30mm thick kota including chase cutting in walls & repairing walls after fixing slab also inclusive of making and rounding off edges, including rubbing polishing complete. ( Base Rate 90 rs Sft Without GST) | 1187.5 | Sqm |  | 0
06.09 | Providing & Fixing 60mm thick inline locking tiles |  | Sqm |  | 0
06.11 | kota stone slabs 30 mm thick in skirting 100 mm height & dado and pillars laid on 12 mm (average) thick cement mortar 1:3 (1 cement 3 coarse sand) and jointed with approved adhesive with pigment to match the shade of the slabs, including rubbing and polishing complete as per EIC .( Base Rate 220 Sft Without GST) | 178.125 | Sqm |  | 0
06.10 | Providing and laying Vitrified tile of approval make, shade as approved by Architect over adequate thickness of mortar (1:4), making joint filled with tile epoxy with approved pigmented to match the shade of tile & laid as per design & drawing approved by Architect for various thick of tiles as per EIC.( Terrace, Water Tank)
06.10.01 | Vitrified tiles ( basic rate Rs. 55 per sqft ) | 1533.87 | Sqm |  | 0
6.12 | Providing and fixing stone of required size and shape of approved shade, colour and texture in required size .20 mm thick Mirror polished granite and machine edge cut in walls, pillars, steps, Shelves, Sills Counters, Floors etc. laid on 40mm (Av.) thick base of cement mortar 1:3 (1 cement : 3 coarse sand) jointing with white cement mortar 1:2 (1white cement : 2 marble dust) with pigment to match the shade of the marble slab including grinding, rubbing and polishing complete. Rajasthan Black Above 3601 Cm2 Slabs ( Base Rate 220 Sft Without GST) | 1000 | Sqm |  | 0
Part VII | FINISHING WORK
Preamble
The rates for all Finishing work include:
i | Hacking and roughening of concrete or other surfaces in contact with surface for bondage.
ii | Using chicken mesh of approved quality wherever required
iii | Making all projections, recess , grooves, cornices and elevation features
iv | Holes (cut and formed or left) for fixing, pipes, bolts and other inserts and making good including grouting if necessary.
v | Forming chases for edges of concrete floors or other units, for sealing in waterproofing layers etc.
vi | Necessary curing & protection
vii | Making all patterns, shape and figures with different shades as per the approved design.
viii | Using necessary clamps, cramps, anchors, hold fast of approved stainless steel grade
ix | Cleaning the existing surface ( new / old) by using necessary cleaning materials as approved
x | Joint treatment with appropriate materials as approved
xi | All lead lift, loading, unloading, cartage, handling and storage.
07.01 | Providing & applying 12 / 15 mm thick cement plaster water proof to walls, columns, piers etc. in cement mortar 1 : 5 (1 cement : 5 fine and coarse sand mix in equal proportions) add with waterproofing chimical applied, finished smooth and cured including fixing chicken wire mesh to junctions of concrete and masonry work and wall conduite and other locations where called for including cutting to required sizes side laps of minimum 75 mm and fixing in position etc. hacking, curing, making grooves / bands wherever required complete. The rate shall includes the cost of scaffolding for all height & chicken wire mesh complete work in all respect as per direction of EIC. | 14140.8852 | Sqm |  | 0
07.02 | Providing & applying 6 -10 mm thick cement plaster in ceiling, soffits and sides of slabs, columns beams and other concrete surfaces not designated as exposed concrete in cement mortar 1 : 3 (1 cement : 3 fine sand )add with waterproofing chimical applied, finished smooth and cured including hacking, curing, making grooves / bands / drip courses wherever required complete. The rate shall includes the cost of scaffolding for all height complete and complete the work in all respect as per direction of EIC. | 6005 | Sqm |  | 0
07.03 | Providing & applying minimum two coat of White cement based Putty of approved brand to new plastered work on walls & ceiling including with scrapping, sand papering & cleaning of plaster wherever required directed by engineer in-charge. | 13212.617 | Sqm |  | 0
07.04 | Acrylic Emulsion paint (two or more coats) with two coat primer of approved brand to give an even shade on Ceiling & Walls including preparing surfaces with on new surface along with sand papering wherever required. | 13212.617 | Sqm |  | 0
07.09 | Providing and applying washed stone grit plaster on exterior walls height upto tarrace level above ground level, in two layers,under layer 12mm thick rough cement plaster 1:4 (1 cement : 4 coarse sand) mixed with water proofing compound of "CICO No.1 ", furrowing the under layer with scratching tool, applying cement slurry on the under layer @ 2 kg of cement per square meter, top layer 15 mm cement plaster 1:½:2 (1 white cement : ½ coarse sand : 2 stone chipping as per existing 10 mm size and color) in panels, including providing and fixing Aluminum C-Channels of size 10mm x 15mm as per approved pattern, repair to the edges of panels and finishing the grooves, scrubbing and washing to top layer with brushes and water to expose the stone chipping etc. complete as required. (The quoted rate to include making drip moulds etc. as required) as per EIC. | 1906.239 | Sqm |  | 0
07.11 | Supplying and laying 35mm thick rough Red Stone Cladding, Coping, band, border of approved shade & make on wall/ column of approved shade & size with grooves, nosing etc.. over a base of 20 mm thick cement mortar of mix 1 : 4 ( 1 cement : 4 coarse sand ) including making necessary grooves, pointing in with white cement backing applied @ 3kg/m2 and joined with white cement slurry mixed with matching colour pigment to match the shade of Stone as per drawings, including drilling necessary holes and sealing the joints with approved semi gloss weather sealant, polishing on all horizontal & vertical surfaces (Laticrete/ Eagle / Dupont) over all the stone, to provide stain resistant & non-porous surface. | 150 | Sqm |  | 0
Part-VIII | ALUMINIUM WORK
08.01 | Providing and fixing aluminium work for , doors, windows and ventilators with extruded built up standard tubular sections as per design and drawing or as approved of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / panelling, C.P.brass / stainless steel screws including all hardware as per design & specifications, all complete as per architectural drawings and the directions of Engineer-in-charge. Make: Bharuka, Jindal .
08.01.01 | For all portion (Frames, panel, shutter and Louvers, hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required Including all fittings Powder coated aluminium) Powder coated aluminium (minimum thickness of powder coating 50 micron) actual installed section shall be consider for the payment.inclusing Hardware: bead join, glass packer, glazing gaskets, door backset, door handle, hinges, door cylinder, door lock, infill bar locking rod, cleat, counter plate, shoot bolt, tower bolt, threshold bush, slider lock sash, bump stop, flyscreen, lock sash, mesh material, interlock plug, antilift plug, center seal, track count, water protect, glass adaptor, center sealing, Including Cost of hardware, Vendor to approve shop drawings from client before execution.
08.01.01A | For fixed portion & Frames | 11807.7825 | Kg |  | 0
08.01.02 | For all portion (Frames, panel, shutter and Louvers, hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required Including all fittings Powder coated aluminium) Powder coated aluminium (minimum thickness of powder coating 50 micron) actual installed section shall be consider for the payment.inclusing Hardware: bead join, glass packer, glazing gaskets, door backset, door handle, hinges, door cylinder, door lock, infill bar locking rod, cleat, counter plate, shoot bolt, tower bolt, threshold bush, slider lock sash, bump stop, flyscreen, lock sash, mesh material, interlock plug, antilift plug, center seal, track count, water protect, glass adaptor, center sealing, Including Cost of hardware, Vendor to approve shop drawings from client before execution. | 2951.9456 | Kg |  | 0
08.02 | Providing and fixing glazing in aluminium window, ventilator shutters and partitions etc. toughened glass panes of 5-6 mm thickness (weight not less than 12.50 kg/SQM) with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . Make: Saint gobain, Modi Guard Including Cost of hardware. | 743.061 | Sqm |  | 0
Part IX | MISCELLANEOUS WORKS
09.06 | Providing, Fabricating, assembling, hoisting / erecting and fixing in position MS Fabrication/Structural Steel Works, at all heights and all levels of all shapes and sizes with all leads and lifts, of Approved make, fabricated from equal and unequal angles, flats, channels, steel hollow box , pips, Solid sections RHS, SHS, tubular Structural box sections, (square, rectangular, tubular hollow sections as per IS 4923 & 1161) confirming to latest IS:808 for the work of MS staircases of any shape, MS gate, Roling Shutter, Elevation grills, Compound wall grills, MS railing, including cutting, riveted, bolted, welding and threading the members as per detailed drawing and design, including cutting and making good masonry and RCC works as per requirement. High strength hooks, bolts ,fasteners for fixing and positioning of members as per design & drawings. Bolts shall confirm to IS : 1367(Part 3)-2002, Gr.-8.8 as per drawings and as directed by engineer in charge The rate shall include 2 coat of zinc chromate red oxide primer and 2 coats of synthetic enamel paint of approved make ( by client / consultant ) over all the surfaces of the steel sections. (Only standard measurements will be paid for as actual cut length used at site). Shop drawings for the connection details shall be prepared by the contractor for the approval of the client/consultant. Rate shall be inclusive of cutting, wastage, welding, bending (shop at site), bolting, riveting wherever necessary, in position welding of required length, grinding, finishing edges, filling the welded spots with paint. Rate shall also include the cost of necessary scaffolding work. It should also include the cost of approved size of zinc coated nut-bolt and any type and size of Anchor fasteners of Hilti or Fisher makes, and cost of necessary scaffolding work and complete the work in all respect as per direction of EIC. Make : TATA (TISCO), SAIL, JSPL, RINL & Apollo Tube | 5000 | Kg |  | 0
09.08 | Providing and Making plinth protection 50mm thick of cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20mm nominal size) over 75mm bed of dry brick ballast 40mm nominal size well rammed and consolidated and grouted with fine sand including finishing the top smooth as per EIC. | 137.55 | Sqm |  | 0
09.11 | SS RAILING WITH: Supply and fixing of railing of height 750 mm. Balusters : Dia 38mm in SS (1% Nickle) @ 26" C/C. Cross Members :15mm 4 nos. in SS (1% Nickle) Handrail : Dia 50mm in SS (1% Nickle) Make: TATA, SAIL, JINDAL | 168.3 | Rmt |  | 0
Extra items
1 | Providing and fixing corner guards made of high-impact resistant steel/aluminum to protect the edges of columns, walls, or other structures from damage. The corner guard should have a minimum length of 1.2 meter and a cross-section of 75 mm x 75 mm, fixed with suitable adhesive or fasteners as per manufacturer’s specifications and complete as directed by the engineer in charge | 82 | Nos |  | 0
2 | P/F 6mm thk. Mirror ( with 3mm X 3mm bevelled edge) of approved make adhesive bonded to 12mm thk. Marine plywood fixed to existing wall surface with 25mm diameter SS 316 studs as per drawing, including preparation of the base surface for mounting of ply including sides of backing marine ply finished with PU finish (ICA, Pidilite or equivalent make) match to adjacent wall colour & work to be complete in all respects as per detail drawing including providing cut-outs wherever necessary as per MEP requirements. | 50.976 | Sqm
| TOTAL |  |  |  | 0
GST 18%
GRAND TOTAL

## Beams (hidden)
BEAM & SLAB RCC Qty
S.No. | Description |  | Length | Width | Height | Cum
Ground Floor
1 | Beam 1' |  | 718.4 | 0.3 | 0.45 | 96.984
2 | Beam 9" |  | 62.4 | 0.23 | 0.45 | 6.4584
3 | Floor |  | 1834 |  | 0.15 | 275.1
4 | Slab |  | 1873 |  | 0.15 | 280.95
First Floor
1 | Beam 1' |  | 818 | 0.3 | 0.45 | 110.43
2 | Beam 9" |  | 62.4 | 0.23 | 0.45 | 6.4584
3 | Floor |  | 1873 |  | 0.15 | 280.95
4 | Slab |  | 1873 |  | 0.15 | 280.95
Second Floor
1 | Beam 1' |  | 818 | 0.3 | 0.45 | 110.43
2 | Beam 9" |  | 62.4 | 0.23 | 0.45 | 6.4584
3 | Floor |  | 1873 |  | 0.15 | 280.95
4 | Slab |  | 1873 |  | 0.15 | 280.95
Terrace
1 | Beam 1' |  | 160.6 | 0.3 | 0.45 | 21.681
2 | Floor |  | 1873 |  | 0.15 | 280.95
3 | Slab |  | 386 |  | 0.15 | 57.9
| Total Beams 1' |  |  |  |  | 339.525
| Total Beams 9" |  |  |  |  | 19.3752
| Total RCC Slab |  |  |  |  | 900.75
BEAM & SLAB Shuttering
S.No. | Description | Nos | Length | Width | Height | Sqm
Ground Floor
1 | Beam 1' | 1 | 718.4 | 0.3 |  | 215.52
2 | Beam 1' | 2 | 718.4 |  | 0.45 | 646.56
3 | Beam 9" | 1 | 62.4 | 0.23 |  | 14.352
4 | Beam 9" | 2 | 62.4 |  | 0.45 | 56.16
5 | Slab | 1 | 1873 |  |  | 1873
First Floor
1 | Beam | 1 | 818 | 0.3 |  | 245.4
2 | Beam | 2 | 818 |  | 0.45 | 736.2
3 | Beam 9" | 1 | 62.4 | 0.23 |  | 14.352
4 | Beam 9" | 2 | 62.4 |  | 0.45 | 56.16
5 | Slab | 1 | 1873 |  |  | 1873
Second Floor
1 | Beam | 1 | 818 | 0.3 |  | 245.4
2 | Beam | 2 | 818 |  | 0.45 | 736.2
3 | Beam 9" | 1 | 62.4 | 0.23 |  | 14.352
4 | Beam 9" | 2 | 62.4 |  | 0.45 | 56.16
5 | Slab | 1 | 1873 |  |  | 1873
Terrace
1 | Beam | 1 | 160.6 | 0.3 |  | 48.18
2 | Beam | 2 | 160.6 |  | 0.45 | 144.54
3 | Slab | 1 | 386 |  |  | 386
| Total Beams Shuttering 1' |  |  |  |  | 3018
| Total Beams Shuttering 9" |  |  |  |  | 211.536
| Total slab Shuttering |  |  |  |  | 6005

## Staircase (hidden)
RCC Columns Shuttering
S.No. | Description | No. | Length | Width | Height | Qty | Unit
| Stair Type 1 (Middle Common) | 30 Steps | 2 | 0.3 | 0.145
Ground to First
| Excavation |  | 2 | 0.6 | 0.75 | 0.9 | cum
| PCC |  | 2 | 0.6 | 0.15 | 0.18 | cum
| Footing |  | 2 | 0.6 | 0.3 | 0.36 | cum
| Foundation |  | 2 | 0.145 | 0.3 | 0.087 | cum
| Bricks For steps | 30 | 2 | 0.3 | 0.145 | 2.61 | cum
| RCC for Slab | 2 | 4.7 | 2 | 0.125 | 2.35 | cum
|  | 1 | 1.79 | 2 | 0.125 | 0.4475 | cum
| RCC for Landing | 2 | 2 | 2 | 0.125 | 1 | cum
| Shuttering For Footing | 2 | 0.6 |  | 0.3 | 0.36 | sqm
|  | 2 | 2 |  | 0.3 | 1.2 | sqm
| Shuttering For Foundation | 4 |  | 0.145 | 0.3 | 0.174 | sqm
| Shuttering For slab | 2 | 4.7 | 2 |  | 18.8 | sqm
|  | 4 | 4.7 |  | 0.125 | 2.35 | sqm
|  | 1 | 1.79 | 2 |  | 3.58 | sqm
|  | 2 | 1.79 |  | 0.125 | 0.4475 | sqm
| Shuttering For Landing | 2 | 2 | 2 |  | 8 | sqm
|  | 4 | 2 |  | 0.125 | 1 | sqm
First to Second
| Bricks For steps | 30 | 2 | 0.3 | 0.145 | 2.61 | cum
| RCC for Slab | 2 | 4.7 | 2 | 0.125 | 2.35 | cum
|  | 1 | 1.79 | 2 | 0.125 | 0.4475 | cum
| RCC for Landing | 2 | 2 | 2 | 0.125 | 1 | cum
| Shuttering For slab | 2 | 4.7 | 2 |  | 18.8 | sqm
|  | 4 | 4.7 |  | 0.125 | 2.35 | sqm
|  | 1 | 1.79 | 2 |  | 3.58 | sqm
|  | 2 | 1.79 |  | 0.125 | 0.4475 | sqm
| Shuttering For Landing | 2 | 2 | 2 |  | 8 | sqm
|  | 4 | 2 |  | 0.125 | 1 | sqm
Second to third
| Bricks For steps | 30 | 2 | 0.3 | 0.145 | 2.61 | cum
| RCC for Slab | 2 | 4.7 | 2 | 0.125 | 2.35 | cum
|  | 1 | 1.79 | 2 | 0.125 | 0.4475 | cum
| RCC for Landing | 2 | 2 | 2 | 0.125 | 1 | cum
| Shuttering For slab | 2 | 4.7 | 2 |  | 18.8 | sqm
|  | 4 | 4.7 |  | 0.125 | 2.35 | sqm
|  | 1 | 1.79 | 2 |  | 3.58 | sqm
|  | 2 | 1.79 |  | 0.125 | 0.4475 | sqm
| Shuttering For Landing | 2 | 2 | 2 |  | 8 | sqm
|  | 4 | 2 |  | 0.125 | 1 | sqm
| Stair Type 2 (Upper Common) | 20 Steps | 1.5 | 0.3 | 0.145
Ground to First
| Excavation |  | 1.5 | 0.6 | 0.75 | 0.675 | cum
| PCC |  | 1.5 | 0.6 | 0.15 | 0.135 | cum
| Footing |  | 1.5 | 0.6 | 0.3 | 0.27 | cum
| Foundation |  | 1.5 | 0.145 | 0.3 | 0.06525 | cum
| Bricks For steps | 20 | 1.5 | 0.3 | 0.145 | 1.305 | cum
| RCC for Slab | 2 | 1.84 | 1.5 | 0.125 | 0.69 | cum
|  | 2 | 1.76 | 1.5 | 0.125 | 0.66 | cum
| RCC for Landing | 4 | 1.5 | 1.5 | 0.125 | 1.125 | cum
| Shuttering For Footing | 2 |  | 0.6 | 0.3 | 0.36 | sqm
|  | 2 | 1.5 |  | 0.3 | 0.9 | sqm
| Shuttering For Foundation | 4 |  | 0.145 | 0.3 | 0.174 | sqm
| Shuttering For slab | 2 | 1.84 | 1.5 |  | 5.52 | sqm
|  | 4 | 1.84 |  | 0.125 | 0.92 | sqm
|  | 2 | 1.76 | 1.5 |  | 5.28 | sqm
|  | 4 | 1.76 |  | 0.125 | 0.88 | sqm
| Shuttering For Landing | 4 | 1.5 | 1.5 |  | 9 | sqm
|  | 8 | 1.5 |  | 0.125 | 1.5 | sqm
First to Second
| Bricks For steps | 20 | 1.5 | 0.3 | 0.145 | 1.305 | cum
| RCC for Slab | 2 | 1.84 | 1.5 | 0.125 | 0.69 | cum
|  | 2 | 1.76 | 1.5 | 0.125 | 0.66 | cum
| RCC for Landing | 4 | 1.5 | 1.5 | 0.125 | 1.125 | cum
| Shuttering For slab | 2 | 1.84 | 1.5 |  | 5.52 | sqm
|  | 4 | 1.84 |  | 0.125 | 0.92 | sqm
|  | 2 | 1.76 | 1.5 |  | 5.28 | sqm
|  | 4 | 1.76 |  | 0.125 | 0.88 | sqm
| Shuttering For Landing | 4 | 1.5 | 1.5 |  | 9 | sqm
|  | 8 | 1.5 |  | 0.125 | 1.5 | sqm
Second to third
| Bricks For steps | 20 | 1.5 | 0.3 | 0.145 | 1.305 | cum
| RCC for Slab | 2 | 1.84 | 1.5 | 0.125 | 0.69 | cum
|  | 2 | 1.76 | 1.5 | 0.125 | 0.66 | cum
| RCC for Landing | 4 | 1.5 | 1.5 | 0.125 | 1.125 | cum
| Shuttering For slab | 2 | 1.84 | 1.5 |  | 5.52 | sqm
|  | 4 | 1.84 |  | 0.125 | 0.92 | sqm
|  | 2 | 1.76 | 1.5 |  | 5.28 | sqm
|  | 4 | 1.76 |  | 0.125 | 0.88 | sqm
| Shuttering For Landing | 4 | 1.5 | 1.5 |  | 9 | sqm
|  | 8 | 1.5 |  | 0.125 | 1.5 | sqm
| Front Staircases (2) | 2 Sets
Ground
| Excavation | 2 | 10.1 | 0.6 | 0.75 | 9.09 | cum
| PCC | 2 | 10.1 | 0.6 | 0.15 | 1.818 | cum
| RCC Foundation 1 | 2 | 10.1 | 0.6 | 0.3 | 3.636 | cum
| RCC Foundation 2 | 2 | 10.1 | 0.3 | 0.3 | 1.818 | cum
| RCC for wall | 2 | 10.1 | 0.3 | 0.75 | 4.545 | cum
| PCC for Soling | 2 | 22.14 |  | 0.15 | 6.642 | cum
| Soling | 2 | 22.14 |  | 0.45 | 19.926 | cum
| Bricks For steps | 2 | 10.7 | 0.3 | 0.6 | 3.852 | cum
|  | 2 | 11.3 | 0.3 | 0.45 | 3.051 | cum
|  | 2 | 11.9 | 0.3 | 0.3 | 2.142 | cum
|  | 2 | 12.5 | 0.3 | 0.15 | 1.125 | cum
| Shuttering For Foundation 1 | 4 | 10.1 |  | 0.3 | 12.12 | sqm
|  | 4 |  | 0.6 | 0.3 | 0.72 | sqm
| Shuttering For Foundation 2 | 4 | 10.1 |  | 0.3 | 0.36 | sqm
|  | 4 |  | 0.3 | 0.3 | 0.36
| Shuttering For Wall | 4 | 10.1 |  | 0.75 | 30.3 | sqm
| Left Staircase (1) | 1
Ground
| Excavation | 1 | 12.3 | 0.6 | 0.75 | 5.535 | cum
| PCC | 1 | 12.3 | 0.6 | 0.15 | 1.107 | cum
| RCC Foundation 1 | 1 | 12.3 | 0.6 | 0.3 | 2.214 | cum
| RCC Foundation 2 | 1 | 12.3 | 0.3 | 0.3 | 1.107 | cum
| RCC for wall | 1 | 12.3 | 0.3 | 0.75 | 2.7675 | cum
| PCC for Soling | 1 | 15.4 |  | 0.15 | 2.31 | cum
| Soling | 1 | 15.4 |  | 0.45 | 6.93 | cum
| Bricks For steps | 1 | 6.3 | 0.3 | 0.6 | 1.134 | cum
|  | 1 | 6.3 | 0.3 | 0.45 | 0.8505 | cum
|  | 1 | 6.3 | 0.3 | 0.3 | 0.567 | cum
|  | 1 | 6.3 | 0.3 | 0.15 | 0.2835 | cum
| Shuttering For Foundation 1 | 2 | 12.3 |  | 0.3 | 7.38 | sqm
|  | 2 |  | 0.6 | 0.3 | 0.36 | sqm
| Shuttering For Foundation 2 | 2 | 12.3 |  | 0.3 | 7.38 | sqm
|  | 2 |  | 0.3 | 0.3 | 0.18 | sqm
| Shuttering For Wall | 2 | 12.3 |  | 0.75 | 18.45 | sqm
| Backside Staircase | 1
Ground
| Excavation | 1 | 10.5 | 0.6 | 0.75 | 4.725 | cum
| PCC | 1 | 10.5 | 0.6 | 0.15 | 0.945 | cum
| RCC Foundation 1 | 1 | 10.5 | 0.6 | 0.3 | 1.89 | cum
| RCC Foundation 2 | 1 | 10.5 | 0.3 | 0.3 | 0.945 | cum
| RCC for wall | 1 | 10.5 | 0.3 | 0.75 | 2.3625 | cum
| PCC for Soling | 1 | 8.2 |  | 0.15 | 1.23 | cum
| Soling | 1 | 8.2 |  | 0.45 | 3.69 | cum
| Bricks For steps | 1 | 7.5 | 0.3 | 0.6 | 1.35 | cum
|  | 1 | 7.5 | 0.3 | 0.45 | 1.0125 | cum
|  | 1 | 7.5 | 0.3 | 0.3 | 0.675 | cum
|  | 1 | 7.5 | 0.3 | 0.15 | 0.3375 | cum
| Shuttering For Foundation 1 | 2 | 10.5 |  | 0.3 | 6.3 | sqm
|  | 2 |  | 0.6 | 0.3 | 0.36 | sqm
| Shuttering For Foundation 2 | 2 | 10.5 |  | 0.3 | 6.3 | sqm
|  | 2 |  | 0.3 | 0.3 | 0.18 | sqm
| Shuttering For Wall | 2 | 10.5 |  | 0.75 | 15.75 | sqm
| Total Excavation |  |  |  |  | 20.925
| Total PCC |  |  |  |  | 4.185
| Total RCC for Foundation |  |  |  |  | 12.3922
| Total RCC Slab |  |  |  |  | 12.4425
| Total RCC landings |  |  |  |  | 6.375
| Total RCC Wall |  |  |  |  | 9.675
| Total Brick Work |  |  |  |  | 28.125
| Shuttering for Foundation |  |  |  |  | 45.168
| Shuttering for slabs |  |  |  |  | 111.5725
| Shuttering for landings |  |  |  |  | 53.5
| Shuttering for wall |  |  |  |  | 64.5

## Columns (hidden)
RCC Columns (Total Columns =82)
S.No. | Description | No. | Length | Width | Height | Volume | Foundation deduction in filling
| F1 Type | 7 | 0.3 | 0.45
| Excavation | 7 | 2.1 | 2.1 | 2 | 61.74
| PCC | 7 | 2.1 | 2.1 | 0.15 | 4.6305
| RCC Footing | 7 | 1.95 | 1.95 | 0.5 | 13.3087 | 13.3087
| RCC Column Till NGL | 7 | 0.3 | 0.45 | 1.35 | 1.2757 | 1.2757
| RCC Column RCC Column Till First Floor | 7 | 0.3 | 0.45 | 4.8 | 4.536
| RCC Column RCC Column Till Second Floor | 7 | 0.3 | 0.45 | 4.05 | 3.8272
| RCC Column Till Third Floor | 7 | 0.3 | 0.45 | 4.05 | 3.8272
| RCC Column Till Terrace | 7 | 0.3 | 0.45 | 2.7 | 2.5515
| F2 Type | 8 | 0.3 | 0.6
| Excavation | 8 | 2.7 | 2.7 | 2 | 116.64
| PCC | 8 | 2.7 | 2.7 | 0.15 | 8.748
| RCC Footing | 8 | 2.55 | 2.55 | 0.6 | 31.212 | 31.212
| RCC Column Till NGL | 8 | 0.3 | 0.6 | 1.25 | 1.8 | 1.8
| RCC Column Till First Floor | 8 | 0.3 | 0.6 | 4.8 | 6.912
| RCC Column Till Second Floor | 8 | 0.3 | 0.6 | 4.05 | 5.832
| RCC Column Till Third Floor | 8 | 0.3 | 0.6 | 4.05 | 5.832
| RCC Column Till Terrace | 8 | 0.3 | 0.6 | 2.7 | 3.888
| F3 Type | 5 | 0.3 | 0.6
| Excavation | 5 | 3 | 3 | 2 | 90
| PCC | 5 | 3 | 3 | 0.15 | 6.75
| RCC Footing | 5 | 2.85 | 2.85 | 0.7 | 28.4287 | 28.4287
| RCC Column Till NGL | 5 | 0.3 | 0.6 | 1.15 | 1.035 | 1.035
| RCC Column Till First Floor | 5 | 0.3 | 0.6 | 4.8 | 4.32
| RCC Column Till Second Floor | 5 | 0.3 | 0.6 | 4.05 | 3.645
| RCC Column Till Third Floor | 5 | 0.3 | 0.6 | 4.05 | 3.645
| RCC Column Till Terrace | 5 | 0.3 | 0.6 | 2.7 | 2.43
| F4 Type | 4 | 0.3 | 0.6
| Excavation | 4 | 3.45 | 3.45 | 2 | 95.22
| PCC | 4 | 3.45 | 3.45 | 0.15 | 7.1415
| RCC Footing | 4 | 3.15 | 3.15 | 0.8 | 31.752 | 31.752
| RCC Column Till NGL | 4 | 0.3 | 0.6 | 1.05 | 0.756 | 0.756
| RCC Column Till First Floor | 4 | 0.3 | 0.6 | 4.8 | 3.456
| RCC Column Till Second Floor | 4 | 0.3 | 0.6 | 4.05 | 2.916
| RCC Column Till Third Floor | 4 | 0.3 | 0.6 | 4.05 | 2.916
| RCC Column Till Terrace | 4 | 0.3 | 0.6 | 2.7 | 1.944
| F5 Type | 16 | 0.3 | 0.6
| Excavation | 16 | 3.75 | 3.75 | 2 | 450
| PCC | 16 | 3.75 | 3.75 | 0.15 | 33.75
| RCC Footing | 16 | 3.45 | 3.45 | 0.9 | 171.396 | 171.396
| RCC Column Till NGL | 16 | 0.3 | 0.6 | 1.85 | 5.328 | 5.328
| RCC Column Till First Floor | 16 | 0.3 | 0.6 | 4.8 | 13.824
| RCC Column Till Second Floor | 16 | 0.3 | 0.6 | 4.05 | 11.664
| RCC Column Till Third Floor | 16 | 0.3 | 0.6 | 4.05 | 11.664
| RCC Column Till Terrace | 16 | 0.3 | 0.6 | 2.7 | 7.776
| Section (01-01) | 2 | 0.3 | 0.45
| Excavation | 1 | 6.24 | 3 | 2 | 37.44
| PCC | 1 | 6.24 | 3 | 0.15 | 2.808
| RCC Footing | 1 | 6.09 | 2.85 | 0.75 | 13.0174 | 13.0174
| RCC Column Till NGL | 2 | 0.3 | 0.45 | 1.1 | 0.297 | 0.297
| RCC Column Till First Floor | 2 | 0.3 | 0.45 | 4.8 | 1.296
| RCC Column Till Second Floor | 2 | 0.3 | 0.45 | 4.05 | 1.0935
| RCC Column Till Third Floor | 2 | 0.3 | 0.45 | 4.05 | 1.0935
| RCC Column Till Terrace | 2 | 0.3 | 0.45 | 2.7 | 0.729
| Section (02-02) Upside Lift | 4 | 0.3 | 0.45
| Excavation | 1 | 5.21 | 7.4 | 1.2 | 46.2648
| PCC | 1 | 5.21 | 7.4 | 0.15 | 5.7831
| RCC Footing | 1 | 5.06 | 7.23 | 0.6 | 21.9503 | 21.9503
| RCC Foundation Till FFL | 1 | 20.8 | 0.23 | 0.55 | 2.6312 | 2.6312
| Brick Masonry | 1 | 20.8 | 0.23 | 15.6 | 74.6304
| RCC Column Till First Floor | 4 | 0.3 | 0.45 | 4.8 | 2.592
| RCC Column Till Second Floor | 4 | 0.3 | 0.45 | 4.05 | 2.187
| RCC Column Till Third Floor | 4 | 0.3 | 0.45 | 4.05 | 2.187
| RCC Column Till Terrace | 4 | 0.3 | 0.45 | 2.7 | 1.458
| Section (03-03) | 16 | 0.6 | 0.6
| Excavation | 1 | 41.225 | 3 | 2 | 247.35
| PCC | 1 | 41.225 | 3 | 0.15 | 18.5512
| RCC Footing | 1 | 41.075 | 2.85 | 0.6 | 70.2383 | 70.2383
| RCC Column Till NGL | 16 | 0.6 | 0.6 | 1.25 | 7.2 | 7.2
| RCC Column Till First Floor | 16 | 0.6 | 0.6 | 4.8 | 27.648
| RCC Column Till Second Floor | 16 | 0.6 | 0.6 | 4.05 | 23.328
| RCC Column Till Third Floor | 16 | 0.6 | 0.6 | 4.05 | 23.328
| RCC Column Till Terrace | 16 | 0.6 | 0.6 | 2.7 | 15.552
| Section (04-04) | 5 | 0.45,0.6 | 0.3
| Excavation | 1 | 42.1 |  | 2 | 84.2
| PCC | 1 | 42.1 |  | 0.15 | 6.315
| RCC Footing | 1 | 40 |  | 0.75 | 30 | 30
| RCC Column Till NGL (0.45*0.3) | 4 | 0.45 | 0.3 | 1.1 | 0.594 | 0.594
| (0.6*0.3) | 1 | 0.6 | 0.3 | 1.1 | 0.198 | 0.198
| RCC Column Till First Floor | 4 | 0.45 | 0.3 | 4.8 | 2.592
| (0.6*0.3) | 1 | 0.6 | 0.3 | 4.8 | 0.864
| RCC Column Till Second Floor | 4 | 0.45 | 0.3 | 4.05 | 2.187
| (0.6*0.3) | 1 | 0.6 | 0.3 | 4.05 | 0.729
| RCC Column Till Third Floor | 4 | 0.45 | 0.3 | 4.05 | 2.187
| (0.6*0.3) | 1 | 0.6 | 0.3 | 4.05 | 0.729
| RCC Column Till Terrace | 4 | 0.45 | 0.3 | 2.7 | 1.458
| (0.6*0.3) | 1 | 0.6 | 0.3 | 2.7 | 0.486
| Section (05-05) | 9 | 0.45,0.6 | 0.3
| Excavation | 3 | 27.9 |  | 2 | 55.8
| PCC | 3 | 27.9 |  | 0.15 | 4.185
| RCC Footing | 3 | 26 |  | 0.75 | 19.5 | 19.5
| RCC Column Till NGL | 6 | 0.45 | 0.3 | 1.15 | 0.9315 | 0.9315
| (0.6*0.3) | 3 | 0.6 | 0.3 | 1.15 | 0.621 | 0.621
| RCC Column Till First Floor | 6 | 0.45 | 0.3 | 4.8 | 3.888
| (0.6*0.3) | 3 | 0.6 | 0.3 | 4.8 | 2.592
| RCC Column Till Second Floor | 6 | 0.45 | 0.3 | 4.05 | 3.2805
| (0.6*0.3) | 3 | 0.6 | 0.3 | 4.05 | 2.187
| RCC Column Till Third Floor | 6 | 0.45 | 0.3 | 4.05 | 3.2805
| (0.6*0.3) | 3 | 0.6 | 0.3 | 4.05 | 2.187
| RCC Column Till Terrace | 6 | 0.45 | 0.3 | 2.7 | 2.187
| (0.6*0.3) | 3 | 0.6 | 0.3 | 2.7 | 1.458
| Section (06-06) | 2 | 0.3 | 0.45
| Excavation | 1 | 6.15 | 3.15 | 1 | 19.3725
| PCC | 1 | 6.15 | 3.15 | 0.15 | 2.9059
| RCC Footing | 1 | 6 | 3 | 0.8 | 14.4 | 14.4
| RCC Column Till NGL | 2 | 0.3 | 0.45 | 1.05 | 0.2835 | 0.2835
| RCC Column Till First Floor | 2 | 0.3 | 0.45 | 4.8 | 1.296
| RCC Column Till Second Floor | 2 | 0.3 | 0.45 | 4.05 | 1.0935
| RCC Column Till Third Floor | 2 | 0.3 | 0.45 | 4.05 | 1.0935
| RCC Column Till Terrace | 2 | 0.3 | 0.45 | 2.7 | 0.729
| Section (07-07) Down Lift | 4
| Excavation | 1 | 5.6 | 5.5 | 1.2 | 36.96
| PCC | 1 | 5.6 | 5.5 | 0.15 | 4.62
| RCC Footing | 1 | 5.6 | 5.5 | 0.6 | 18.48 | 18.48
| RCC Column Till FFL | 1 | 13.43 | 0.23 | 0.55 | 1.6989 | 1.6989
| Brick Masonry | 1 | 13.43 | 0.23 | 15.6 | 48.1868
| RCC Column Till First Floor | 4 | 0.3 | 0.45 | 4.8 | 2.592
| RCC Column Till Second Floor | 4 | 0.3 | 0.45 | 4.05 | 2.187
| RCC Column Till Third Floor | 4 | 0.3 | 0.45 | 4.05 | 2.187
| RCC Column Till Terrace | 4 | 0.3 | 0.45 | 2.7 | 1.458
| Total RCC Footing |  |  |  |  | 487.2982 | 488.3332
| Total Excavation |  |  |  |  | 1340.9873
| Total PCC |  |  |  |  | 106.1882
| Total RCC |  |  |  |  | 255.861
82

## Column Shuttering (hidden)
RCC Columns Shuttering
S.No. | Description | No. | Length | Width | Height | Area
| F1 Type | 7 | 0.3 | 0.45
| RCC Footing Shuttering | 14 | 1.95 |  | 0.5 | 13.65
|  | 14 |  | 1.95 | 0.5 | 13.65
| RCC Foundation Till NGL Shuttering | 14 | 0.3 |  | 1.85 | 7.77
|  | 14 |  | 0.45 | 1.85 | 11.655
| RCC Column RCC Column Till First Floor Shuttering | 14 | 0.3 |  | 5.25 | 22.05
|  | 14 |  | 0.45 | 5.25 | 33.075
| RCC Column RCC Column Till Second Floor Shuttering | 14 | 0.3 |  | 4.5 | 18.9
|  | 14 |  | 0.45 | 4.5 | 28.35
| RCC Column Till Third Floor Shuttering | 14 | 0.3 |  | 4.5 | 18.9
|  | 14 |  | 0.45 | 4.5 | 28.35
| RCC Column Till Terrace Shuttering | 14 | 0.3 |  | 3.15 | 13.23
|  | 14 |  | 0.45 | 3.15 | 19.845
| F2 Type | 8 | 0.3 | 0.6
| RCC Footing Shuttering | 16 | 2.55 |  | 0.6 | 24.48
|  | 16 |  | 2.55 | 0.6 | 24.48
| RCC Foundation Till NGL Shuttering | 16 | 0.3 |  | 1.85 | 8.88
|  | 16 | 0.3 | 0.6 | 1.85 | 17.76
| RCC Column RCC Column Till First Floor Shuttering | 16 | 0.3 |  | 5.25 | 25.2
|  | 16 |  | 0.6 | 5.25 | 50.4
| RCC Column RCC Column Till Second Floor Shuttering | 16 | 0.3 |  | 4.5 | 21.6
|  | 16 |  | 0.6 | 4.5 | 43.2
| RCC Column Till Third Floor Shuttering | 16 | 0.3 |  | 4.5 | 21.6
|  | 16 |  | 0.6 | 4.5 | 43.2
| RCC Column Till Terrace Shuttering | 16 | 0.3 |  | 3.15 | 15.12
|  | 16 |  | 0.6 | 3.15 | 30.24
| F3 Type | 5 | 0.3 | 0.6
| RCC Footing Shuttering | 10 | 2.85 |  | 0.7 | 19.95
|  | 10 |  | 2.85 | 0.7 | 19.95
| RCC Foundation Till NGL Shuttering | 10 | 0.3 |  | 1.85 | 5.55
|  | 10 |  | 0.6 | 1.85 | 11.1
| RCC Column RCC Column Till First Floor Shuttering | 10 | 0.3 |  | 5.25 | 15.75
|  | 10 |  | 0.6 | 5.25 | 31.5
| RCC Column RCC Column Till Second Floor Shuttering | 10 | 0.3 |  | 4.5 | 13.5
|  | 10 |  | 0.6 | 4.5 | 27
| RCC Column Till Third Floor Shuttering | 10 | 0.3 |  | 4.5 | 13.5
|  | 10 |  | 0.6 | 4.5 | 27
| RCC Column Till Terrace Shuttering | 10 | 0.3 |  | 3.15 | 9.45
|  | 10 |  | 0.6 | 3.15 | 18.9
| F4 Type | 4 | 0.3 | 0.6
| RCC Footing Shuttering | 8 | 3.15 |  | 0.8 | 20.16
|  | 8 |  | 3.15 | 0.8 | 20.16
| RCC Foundation Till NGL Shuttering | 8 | 0.3 |  | 1.85 | 4.44
|  | 8 |  | 0.6 | 1.85 | 8.88
| RCC Column RCC Column Till First Floor Shuttering | 8 | 0.3 |  | 5.25 | 12.6
|  | 8 |  | 0.6 | 5.25 | 25.2
| RCC Column RCC Column Till Second Floor Shuttering | 8 | 0.3 |  | 4.5 | 10.8
|  | 8 |  | 0.6 | 4.5 | 21.6
| RCC Column Till Third Floor Shuttering | 8 | 0.3 |  | 4.5 | 10.8
|  | 8 |  | 0.6 | 4.5 | 21.6
| RCC Column Till Terrace Shuttering | 8 | 0.3 |  | 3.15 | 7.56
|  | 8 |  | 0.6 | 3.15 | 15.12
| F5 Type | 16 | 0.3 | 0.6
| RCC Footing | 32 | 3.45 |  | 0.9 | 99.36
|  | 32 |  | 3.45 | 0.9 | 99.36
| RCC Foundation Till NGL | 32 | 0.3 |  | 1.85 | 17.76
|  | 32 |  | 0.6 | 1.85 | 35.52
| RCC Column Till First Floor | 32 | 0.3 |  | 5.25 | 50.4
|  | 32 |  | 0.6 | 5.25 | 100.8
| RCC Column Till Second Floor | 32 | 0.3 |  | 4.5 | 43.2
|  | 32 |  | 0.6 | 4.5 | 86.4
| RCC Column Till Third Floor | 32 | 0.3 |  | 4.5 | 43.2
|  | 32 |  | 0.6 | 4.5 | 86.4
| RCC Column Till Terrace | 32 | 0.3 |  | 3.15 | 30.24
|  | 32 |  | 0.6 | 3.15 | 60.48
| Section (01-01) | 2 | 0.3 | 0.45
| RCC Footing | 2 | 6.09 |  | 0.75 | 9.135
|  | 2 |  | 2.85 | 0.75 | 4.275
| RCC Foundation Till NGL | 4 | 0.3 |  | 1.85 | 2.22
|  | 4 |  | 0.45 | 1.85 | 3.33
| RCC Column Till First Floor | 4 | 0.3 |  | 5.25 | 6.3
|  | 4 |  | 0.45 | 5.25 | 9.45
| RCC Column Till Second Floor | 4 | 0.3 |  | 4.5 | 5.4
|  | 4 |  | 0.45 | 4.5 | 8.1
| RCC Column Till Third Floor | 4 | 0.3 |  | 4.5 | 5.4
|  | 4 |  | 0.45 | 4.5 | 8.1
| RCC Column Till Terrace | 4 | 0.3 |  | 3.15 | 3.78
|  | 4 |  | 0.45 | 3.15 | 5.67
| Section (02-02) Upside Lift | 4 | 0.3 | 0.45
| RCC Footing | 2 | 5.06 |  | 0.6 | 6.072
|  | 2 |  | 7.23 | 0.6 | 8.676
| RCC Foundation Till FFL | 2 | 20.8 |  | 1.8 | 74.88
|  | 2 |  | 0.23 | 1.8 | 0.828
| RCC Column Till First Floor | 8 | 0.3 |  | 5.25 | 12.6
|  | 8 |  | 0.45 | 5.25 | 18.9
| RCC Column Till Second Floor | 8 | 0.3 |  | 4.5 | 10.8
|  | 8 |  | 0.45 | 4.5 | 16.2
| RCC Column Till Third Floor | 8 | 0.3 |  | 4.5 | 10.8
|  | 8 |  | 0.45 | 4.5 | 16.2
| RCC Column Till Terrace | 8 | 0.3 |  | 3.15 | 7.56
|  | 8 |  | 0.45 | 3.15 | 11.34
| Section (03-03) | 16 | 0.6 | 0.6
| RCC Footing | 2 | 41.075 |  | 0.6 | 49.29
|  | 2 |  | 2.85 | 0.6 | 3.42
| RCC Foundation Till NGL | 32 | 0.6 |  | 1.85 | 35.52
|  | 32 |  | 0.6 | 1.85 | 35.52
| RCC Column Till First Floor | 32 | 0.6 |  | 5.25 | 100.8
|  | 32 |  | 0.6 | 5.25 | 100.8
| RCC Column Till Second Floor | 32 | 0.6 |  | 4.5 | 86.4
|  | 32 |  | 0.6 | 4.5 | 86.4
| RCC Column Till Third Floor | 32 | 0.6 |  | 4.5 | 86.4
|  | 32 |  | 0.6 | 4.5 | 86.4
| RCC Column Till Terrace | 32 | 0.6 |  | 3.15 | 60.48
|  | 32 |  | 0.6 | 3.15 | 60.48
| Section (04-04) | 5 | 0.45,0.6 | 0.3
| RCC Footing | 1 | 27.9 |  | 0.75 | 20.925
| RCC Foundation Till NGL (0.45*0.3) | 8 | 0.45 |  | 1.85 | 6.66
|  | 8 |  | 0.3 | 1.85 | 4.44
| (0.6*0.3) | 2 | 0.6 |  | 1.85 | 2.22
|  | 2 |  | 0.3 | 1.85 | 1.11
| RCC Column Till First Floor | 8 | 0.45 |  | 5.25 | 18.9
|  | 8 |  | 0.3 | 5.25 | 12.6
| (0.6*0.3) | 2 | 0.6 |  | 5.25 | 6.3
|  | 2 |  | 0.3 | 5.25 | 3.15
| RCC Column Till Second Floor | 8 | 0.45 |  | 4.5 | 16.2
|  | 8 |  | 0.3 | 4.5 | 10.8
| (0.6*0.3) | 2 | 0.6 |  | 4.5 | 5.4
|  | 2 |  | 0.3 | 4.5 | 2.7
| RCC Column Till Third Floor | 8 | 0.45 |  | 4.5 | 16.2
|  | 8 |  | 0.3 | 4.5 | 10.8
| (0.6*0.3) | 2 | 0.6 |  | 4.5 | 5.4
|  | 2 |  | 0.3 | 4.5 | 2.7
| RCC Column Till Terrace | 8 | 0.45 |  | 3.15 | 11.34
|  | 8 |  | 0.3 | 3.15 | 7.56
| (0.6*0.3) | 2 | 0.6 |  | 3.15 | 3.78
|  | 2 |  | 0.3 | 3.15 | 1.89
| Section (05-05) | 3 | 0.45,0.6 | 0.3
| RCC Footing | 3 | 24.7 |  | 0.75 | 18.525
| RCC Foundation Till NGL | 12 | 0.45 |  | 1.85 | 9.99
|  | 12 |  | 0.3 | 1.85 | 6.66
| (0.6*0.3) | 6 | 0.6 |  | 1.85 | 6.66
|  | 6 |  | 0.3 | 1.85 | 3.33
| RCC Column Till First Floor | 12 | 0.45 |  | 5.25 | 28.35
|  | 12 |  | 0.3 | 5.25 | 18.9
| (0.6*0.3) | 6 | 0.6 |  | 5.25 | 18.9
|  | 6 |  | 0.3 | 5.25 | 9.45
| RCC Column Till Second Floor | 12 | 0.45 |  | 4.5 | 24.3
|  | 12 |  | 0.3 | 4.5 | 16.2
| (0.6*0.3) | 6 | 0.6 |  | 4.5 | 16.2
|  | 6 |  | 0.3 | 4.5 | 8.1
| RCC Column Till Third Floor | 12 | 0.45 |  | 4.5 | 24.3
|  | 12 |  | 0.3 | 4.5 | 16.2
| (0.6*0.3) | 6 | 0.6 |  | 4.5 | 16.2
|  | 6 |  | 0.3 | 4.5 | 8.1
| RCC Column Till Terrace | 12 | 0.45 |  | 3.15 | 17.01
|  | 12 |  | 0.3 | 3.15 | 11.34
| (0.6*0.3) | 6 | 0.6 |  | 3.15 | 11.34
|  | 6 |  | 0.3 | 3.15 | 5.67
| Section (06-06) | 2 | 0.3 | 0.45
| RCC Footing | 1 | 6 |  | 0.8 | 4.8
|  | 1 |  | 3 | 0.8 | 2.4
| RCC Foundation Till NGL | 4 | 0.3 |  | 1.85 | 2.22
|  | 4 |  | 0.45 | 1.85 | 3.33
| RCC Column Till First Floor | 4 | 0.3 |  | 5.25 | 6.3
|  | 4 |  | 0.45 | 5.25 | 9.45
| RCC Column Till Second Floor | 4 | 0.3 |  | 4.5 | 5.4
|  | 4 |  | 0.45 | 4.5 | 8.1
| RCC Column Till Third Floor | 4 | 0.3 |  | 4.5 | 5.4
|  | 4 |  | 0.45 | 4.5 | 8.1
| RCC Column Till Terrace | 4 | 0.3 |  | 3.15 | 3.78
|  | 4 |  | 0.45 | 3.15 | 5.67
| Section (07-07) Down Lift | 4 | 0.3 | 0.45
| RCC Footing | 2 | 5.6 |  | 0.6 | 6.72
|  | 2 |  | 5.5 | 0.6 | 6.6
| RCC Foundation Till FFL | 2 | 13.43 |  | 1.8 | 48.348
|  | 2 |  | 0.23 | 1.8 | 0.828
| RCC Column Till First Floor | 8 | 0.3 |  | 5.25 | 12.6
|  | 8 |  | 0.45 | 5.25 | 18.9
| RCC Column Till Second Floor | 8 | 0.3 |  | 4.5 | 10.8
|  | 8 |  | 0.45 | 4.5 | 16.2
| RCC Column Till Third Floor | 8 | 0.3 |  | 4.5 | 10.8
|  | 8 |  | 0.45 | 4.5 | 16.2
| RCC Column Till Terrace | 8 | 0.3 |  | 3.15 | 7.56
|  | 8 |  | 0.45 | 3.15 | 11.34
| Shuttering in Foundation |  |  |  |  | 852.639
| Shuttering Till first Floor |  |  |  |  | 729.225
| Shuttering above First Floor |  |  |  |  | 1875.483

## PLUMBING ABSTRACT
Plumbing Works
S.No. | Description | Unit | Qty | Rate | Amount
(I) | SANITARY FIXTURES (As per Approved LOM)
1 | Providing & fixing vitreous China floor/wall mounted European W.C. with ‘P’ or ‘S’ trap, with seat with lid, C.P. hinges rubber buffers, with 10 litre capacity machine vitreous china low level cistern with accessories, C.P. handle fixed over a pan of suitable brackets complete including cutting and making good wall and floor wherever required.
a) | White colour EWC,Concealed -Cistern, Seat cover, Twin Flush fittings) | Each | 11
3 | Providing & fixing vitreous china oval (Table top) wash basin 550x400mm dia. for under counter mounting, specially fabricated brackets painted white, 32mm C.P.cast brass bottle trap and pipe to wall with C.P. wall flange and rubber adapter for waste connection complete, including cutting and making good the walls wherever required.
a) | White colour(As per Approved LOM) | Each | 18
4 | Providing & fixing 15mm dia C.P. brass bib tap complete including cutting and making good the walls wherever required. | Each
a) | Two way Bib Cock (As per Approved LOM) | Each | 11
b) | Long body (As per Approved LOM) | Each | 18
5 | Providing & fixing 15mm C.P brass angle valve with C.P. copper connecting pipe 375mm long & nuts, washer and C.P. brass flange complete, including cutting & making good the wall wherever required. ( | Each | 60 |  |  | 60
6 | Providing & fixing 15mm C.P. pillar tap for W.B.() | Each | 18
7 | Providing & fixing C.P brass Health Faucet with CP hose of 1.5 mtr lenght, washer and C.P. brass flange complete, including cutting & making good the wall wherever required. | Each | 11
8 | Providing and fixing 15mm C.P overhead shower with shower arm. ( | Each | 2
9 | Providing and fixing one concealed stop cocks for cold or hot water supply. ( ) | Each | 10
10 | Providing & fixing in position storage type hot water electrical vertical heaters with copper container, insulation, and stove enameled M.S. jacket, thermostatically controlled immersion heater, with pilot lamp, 15/20mm dia inlet with non return valve / gate Valve and 5/20mm dia outlet including making connections complete in all respects.(wall mounted with suitable M.S./GI bolts and nuts)
d) | Capacity 50 litres | Each | 2
Internal Drainage
(II) | SOIL, WASTE, VENT AND RAIN WATER PIPES & FITTINGS
1 | Providing & fixing Type-B uPVC SWR pipe conforming to IS:13592-1992, waste and vent pipes including all fittings, (plain or door) e.g. bends, junctions, cowls, offsets, access pieces etc. jointing with uPVC solvent cement including connection to traps, cutting holes in walls and floors, excavation,refilling and disposal of surplus earth wherever required and making good.
a) | 40 mm dia | Metre | 49.05
b) | 75 mm dia | Metre | 99.05
c) | 110mm dia | Metre | 759
2 | Providing and fixing uPVC (S.W.R.) rain water pipes of Type-B conforming to IS:13592-1992 including all fittings with or without access i.e bends, junctions, offsets, etc., and jointing with rubber lubricant and clips (uPVC), including cutting holes in walls and floors connection with rain water khurras etc. , (rubber rings conform to I.S. 5382) wherever required and making good the same, complete as directed by the Engineer-in-Charge.
c) | 160mm outer dia. | Metre | 279.4
3 | Providing & fixing uPVC deep seal P or S trap of self cleansing design with or without vent arm with provision for connecting uPVC inlet fitting complete, including cost of cutting and making good the walls and floors wherever required.
a) | For 110mm inlet and110mm outlet. | Each | 111
4 | Providing & fixing cement concrete 1:2:4 mix (1 cement : 2 coarse sand: 4 stone aggregate 20mm and down gauge) 75mm in bed and pipe.
a) | For 110mm, 75mm and 50mm dia pipes under floor including centering & shuttering wherever required, all round for uPVC Pipes. | Metre | 90.05
b) | For haunching of 150mm dia RCC pipes and concrete bed of 100 MM thickness | Metre | 165.2
5 | Providing and fixing making Khurras with average minimum thickness of 5cm Cement Concrete 1:2:4 ( 1 Cement : 2 Coarse Sand : 4 Graded Stone Aggregate) over PVC sheet 1mx1mx400 micron, finished with 12mm Cement Plaster 1:3 (1 Cement : 3 Coarse Sand) and a coat of neat cement rounding the edges and making & finishing complete.
a) | For 75mm dia outlet with vertical C.I grating. | Each | 5
c) | For 160mm dia outlet with vertical C.I grating. | Each | 5
6 | Providing and fixing 125mm dia Stainless steel ring and Grate with groove locking system, ring to be embedded in floor with sealent. | Each | 45
7 | Providing & fixing square mouth S.W. gully trap grade ‘A‘ complete with C.I. grating, brick masonry chamber and water tight C.I. cover with frame of 300x300mm size (inside) the weight of cover to be not less than 2.72 kg as per standard design. 150x100mm size P type. | Each | 10
III. | WATER SUPPLY SYSTEM (Internal)
1 | Excavation of trenches of required width for pipes, including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5m including getting out the excavated soil, and then returning soil as required, in layers not exceeding 20cm depth including consolidating each deposited layer by ramming, watering etc. and disposing of surplus excavated soil as directed outside the site to the approved dumping ground.
(a) | In all kinds of soil except hard rock
i) | Pipes, UPVC PIPE etc, not exceeding 80mm dia. | Metre | 451
2 | Providing and fixing Chlorinated polyvinyl Chloride pipes (CPVC) (ASTM F437 & ASTM F438) SDR 13.5 having thermal stability for hot & cold water supply system including all CPVC fitting like plain & brass threaded fittings including cutting and chasing in walls and floors and repairing these in good conditions. This includes jointing pipe & fittings one step with the CPVC solvent cement & testing of joints complete as per direction of the Engineer in-charge
b) | 20mm dia | Metre | 527.92
c) | 25mm dia | Metre | 187.7
d) | 32mm dia | Metre | 35.6
e) | 40mm dia | Metre | 109.45
f) | 50mm dia | Metre | 87
3 | Providing and fixing insulation over hot/cold water pipes embedded with one layer of 9mm thick nitrile rubber fome tube & secondery wrapped around the nitrole rubber tube plastic grip tape complete as per Manufactuer's specifications
b) | For 20mm dia pipe or equivalent dia | Metre | 75.65
c) | For 25mm dia pipe or equivalent dia | Metre | 23.2
d) | For 32mm dia pipe or equivalent dia | Metre | 21.15
4 | Providing and fixing brass/bronze lever operated ball valve of full flow with stainless steel ball (AISI 304 and spindle AISI 410) with setting and gland of superior quality, including providing and fixing FABT/MABT of suitable size, having minimum working pressure of 10 kg/cm2.
a) | 20mm dia | Each |  |  | 0
b) | 25mm dia | Each | 30
d) | 40mm dia | Each | 3
e) | 50mm dia | Each | 4
f) | 63mm dia | Each | 5
IV | Drainage / Sewerage System
1 | Constructing brick masonry catch basin with 100 class designation bricks in cement mortar 1:5 (1 cement: 5 coarse sand), 200m thick foundation concrete 1:5:10 (1 cement: 5 coarse sand: 10 graded stone aggregate 40mm nominal size) inside and outside plaster in cement mortar 1:3 (1 cement: 3 coarse sand). inside finished with floating coat of neat cement, making haunches and channel in cement concrete 1:2:4 (1 cement: 2 coarse sand: 4 graded stone aggregate 20mm nominal size) neatly finished, complete as per standard design including excavation, refilling and disposal of surplus earth.
a) | Size 600x600x600mm inside with precast S.F.R.C. grating of approved design and sample fixed in RCC slab in cement 1:2:4 mix (1 cement: 2 coarse sand: 4 graded stone aggregate 20mm nominal size) including centering, shuttering all complete as per site conditions. | Each | 25
3 | Constructing brick masonry manhole with 100 class designation bricks in cement mortar 1:4 (1 cement : 4 coarse sand), RCC top slab with 1:2:4 mix (1 cement : 2 coarse sand: 4 graded stone aggregate 20mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand; 8 graded stone aggregate 40mm nominal size), inside and outside plastering 12mm thick with cement mortar 1:3 (1 cement:3 coarse sand), finished with a floating coat of neat cement inside and rough plaster on outside and making channels in cement concrete 1:2:4 mix (1 cement : 2 coarse sand: 4 graded stone aggregate 20mm nominal size), neatly finished complete as per standard design including excavation, refilling and disposal of surplus earth. Inside size 90x80cms and 60cms deep including C.I. cover with frame (light duty) 455x610mm internal dimensions total weight of cover and frame to be not less than 38 kg (wt. of cover 23 kg and wt. of frame 15 kg) | Each | 6
1 | Providing & fixing white vitreous china flat back urinal large (semi stall) of size 635x395x420mm or equivalent with C.I. hanger and 32mm dia C.P. brass domical waste, 32mm dia cast bottle trap and pipe to wall with C.P. flange complete including cutting and making good the wall and making necessary connections to the flushing system.
Providing &amp; Fixing of white vitreous china battery based infrared sensor operated urinal of approx. size 610 x 390 x 370 mm having pre &amp; post flushing with water (250 ml &amp; 500 ml consumption), having water inlet from back side, including fixing to wall with suitable brackets all as per manufacturers specification and direction of Engineer-in-charge.
a | In white color | Each | 15
2 | Making Hole in exisiting RCC slab & beam via mechanical core cutting machine including clearing of debries & clearing site for work
a) | For 125 mm RCC Slabe | Each | 125
AMOUNT
External Work
4.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains, including dressing of sides and ramming of bottoms, lifting, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 2km.
4.1.1 | All kinds of soil. | cum. | 500
4.2 | Excavating trenches of required width for pipes, cables etc. including excavation for sockets and dressing of sides, ramming of bottoms, depth upto 2.0 M including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cms in depth including consolidating each deposited layer by ramming, watering etc. and disposing of surplus excavated soil as directed, within a lead of 2 km. All kinds of soil.
4.2.1 | Pipes, cables etc. exceeding 80 mm dia but not exceeding 300 mm dia. Metre | Metre | 200
4.2.2 | Pipes, cables etc. exceeding 300 mm dia but not exceeding 600 mm dia. Metre | Metre | 200
4.3 | Sewage & Storm water Pipes:Providing and laying non pressure NP2 class (medium duty) R.C.C. pipes conforming to IS 458 with collars jointed with stiff mixture cement mortar in the proportion of 1:2 (1 cement: 2 fine sand) including testing of joints etc. complete. (all round and upto haunching shall be paid separately)
4.3.1 | 250 mm dia R.C.C. pipe | Metre | 300
4.4 | Hume pipe-Providing, Laying, jointing and testing socketed and spigotted RCC pipes (NP2 class) conforming to IS:458 collars jointed with stiff mixture of cement mortar in the proporation of 1:2 (1 cement : 2 find sand) laid to correct levels below ground in trenches upto required depth including excavation in all kind of soil (hard / soft), dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing protection to pipe all round / haunches as per specification.
4.4.1 | 150 mm dia | Metre | 100
4.6 | Construction of road gully chamber of the following sizes in brick work with bricks of class 75 in cement mortar 1 : 5 (1 cement : 5 find sand) necessary foundation concrete(1 : 4 : 8). Inside & outside plastering 12 mm thick with cement mortar 1 : 3 with a floating a coat of neat cement. Including the RCC top slab for fixing the grating including necessary excavation, dewatering, refilling, watering, ramming, removing, the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing, DI grating with frame.
4.6.1 | Internal size 450 x 450 x 600 mm deep; DI Grating with frame 450 x 450 mm | Each | 10
4.7 | Providing and fixing stoneware gully trap of the following sizes in brick masonary chamber of standard design with first class bricks and trap to be set in cement concrete 1:2:4, both side 12mm thick plastering with floating coat of neat cement. Making necessary connections & providing water tight D.I. cover with frame of 300mm x 300mm internal size. The weight of cover & frame not be less than 8 kg as per standard design. Including necessary excavation, dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required.
4.7.1 | With Sewer bricks with 180 x 150mm size `P' trap | Each | 15
4.8 | Constructing brick masonry manhole in cement mortar 1:4 (1 cement : 4 coarse sand) RCC top slab with 1:2:4 mix ( 1 cement: 2 coarse sand: 4 graded stone aggregate 20 mm nominal size) foundation concrete 1:4:8 mix (1 cement: 4 coarse sand: 8 graded stone aggregate 40 mm nominal size) inside plastering 12 mm thick with cement mortar 1:3 (1 cement: 3 coarse sand) and outside plastering finished with a floating coat of neat cement making channels in cement concrete 1:2:4 mix (1 cement: 2 coarse sand: 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per approved drawing and specification.
4.8.1 | Inside size 90x80 cms and 60 cms deep including CI cover/grating with frame (Light duty) 610x455mm internal diamesions total weight of cover and frame to be not less than 38 kg ( weight of cover 23 kg and weight of frame 15 kg) with FPS bricks.
4.8.1.1 | Manhole to be constructed With Sewer bricks | Each | 5
4.8.2 | Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (medium duty) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) :
4.8.2.1 | Manhole to be constructed With Sewer bricks | Each | 2
4.11 | Providing orange colour safety foot rest of minimum 6 mm thick plastic encapsulated on 12mm dia steel bar having minimun cross section as 23 mm x 25 mm and over all minimum length 263mm and width as 165mm with minimum 112mm space between protruded legs having 2mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and heaving manufacture"s permanent identification mark to be visible even after fixing " incluting fixing in manholes with 30x20x15 cm cement concrete block 1:3:6: (1 cement :3 coarse sand :6 graded stone aggregate 20mm nominal size )complete as per design. | each | 50
| TOTAL |  |  |  | 0
GST 18%
GRAND TOTAL

## Electrical ABSTRACT
Electrical Works
S.No. | DESCRIPTION | UNIT | Office Room | Lab 1 | Lab 2 | Lab 3 | Male Toilet | Female Toilet | Corridor | Incubation Center Total | Room | Luggage Room | Warden Room | Toilet | Stair | Corridor | QTY. | Rate | AMOUNT
Internal Wiring
1 | Point wiring for switch controlled primary light points with 3x2.5 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in 25mm dia heavy class recessed uPVC and surface MS electrical conduiting as per requiremment in system conduiting including the cost of cutting / making good chases / saddling in brick /concreat if required work and including the cost of supplying and fixing modular grid plate mounted 240 volt 6 Amp. control switch housed in minimum 1mm thick GI box as per the no of ways as approve Drg and make .Approved moulded cover plate including the cost of loop earthing with 2.5 sq.mm. FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires complete as per specifications and as required.By providing 4/ 6/8/12 way switch board as required. | Nos. | 1 | 12 | 10 | 12 | 4 | 4 | 15 |  | 3 | 2 | 5 | 8 | 1 | 21 | 55
2 | Point wiring for Secondary light points with 3x2.5 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in 25mm dia heavy class recessed uPVC and surface MS electrical conduiting and JB as per requiremment in system conduiting including the cost of cutting / making good chases / saddling in brick /concreat if required . | Nos. | 1 | 8 | 8 | 8 | 3 | 3 | 5 |  | 0 | 4 |  | 2 | 2 | 16 | 455
3 | Point wiring for fan points with 3x2.5 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in 25 mm dia heavy class uPVC recessed and / or surface MS conduiting system including the cost of cutting / making good chases in brick work and including the cost of supplying and fixing modular grid plate mounted 240volt 6Amp. control switch with provision for electronic /capacitor regulator, housed in minimum 1mm thick GI boxes provided respective for 4/6/8/12 way swich bordwith modular cover plate as per Approved shop drawing . | Nos. | [14 empty] | 128
4 | Point wiring for Exhaust fan points with 3x2.5 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in 25 mm dia heavy class uPVC recessed and / or surface MS conduiting system including the cost of cutting / making good chases in brick work and including the cost of supplying and fixing modular grid plate mounted 240volt 6Amp. 5 pin combined shutters socket outlet near the fan and 240V 6 amps providing GI box . control switch at convenient location near room entrance providing as per approve drawing. | [15 empty] | 20
5 | Point wiring for Twin 6 amps switch socket points points with 3x4 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in 25mm dia heavy class recessed uPVC and surface MS electrical conduiting as per requiremment in system conduiting including the cost of cutting / making good chases / saddling in brick /concreat if required work and including the cost of supplying and fixing modular grid plate mounted 240 volt 6 Amp.5 pin combined shuttered socket outlets alongwith 240 volt 6 amp. control switch housed in GI box as per approve Drg and make including the cost of loop earthing with 2.5 sq.mm. FRLS PVC insulated 660/1100 volt grade stranded copper eart conductor wires complete as per specifications and as required. | Nos. | 1 |  |  |  | 2 | 2 | 4 |  |  | 1 | 1 | 1 |  | 8 | 42
6 | Point wiring for Single 6 amps switch socket points points with 3x4 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in 25mm dia heavy class recessed uPVC and surface MS electrical conduiting as per requiremment in system conduiting including the cost of cutting / making good chases / saddling in brick /concreat if required work and including the cost of supplying and fixing modular grid plate mounted 240 volt 6 Amp.5 pin combined shuttered socket outlets alongwith 240 volt 6 amp. control switch housed in GI box as per approve Drg and make including the cost of loop earthing with 2.5 sq.mm. FRLS PVC insulated 660/1100 volt grade stranded copper eart conductor wires complete as per specifications and as required. | Nos. | [14 empty] | 34
7 | Point wiring for 16 amp socket outlet points (1 outlet wired on 1 circuit) with 3x4 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in 25mm dia heavy class recessed and / or surface uPVC/MS electrical conduiting system including the cost of cutting / making good chases in brick work and including the cost of supplying and fixing modular grid plate mounted 220 volt 16amp. 6 pin combined shuttered socket outlets alongwith 220 volt 16 amp.controlled switch of housed in GI boxes and including the cost of loop earthing with 4 sq.mm. FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires complete as per specifications and as required. | Nos. | 2 | 11 | 6 | 11 | 1 | 1 | 2 |  | 1 | 2 | 1 | 4 |  |  | 42
8 | Point wiring for 16 amp socket outlet points (2 outlet wired on 1 circuit) with 3x6 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in upto first outlet and 4 wire sq.mm.wire for the looped outlet in wires in 25mm dia heavy class recessed and / or surface uPV/MS electrical conduiting system including the cost of cutting / making good chases in brick work and including the cost of supplying and fixing modular grid plate mounted 220volt 16amp. 6 pin combined shuttered socket outlets alongwith 220 volt 16 amp.controlled switch of housed in GI boxes and including the cost of loop earthing with 4 sq.mm. FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires complete as per specifications and as required. | Nos. | [11 empty] | 1 |  | 1 | 22
9 | Point wiring for two way switch controlled light points with 3x2.5 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in 25 mm dia heavy class uPVC /MS recessed and / or surface conduiting system including the cost of cutting / making good chases in brick work and including the cost of supplying and fixing modular grid plate mounted 240volt 6Amp. control switch housed GI boxes with moulded cover plate and including the cost of loop earthing with 2.5 sq.mm. FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires complete as per Drawing and as required. | Nos. | 1 | 16 | 9 | 16 | 1 | 1 | 1 |  | 2 | 6 | 4 | 1 |  |  | 10 |  |  | 69
10 | Point wiring for 16 amp industrial socket outlet points (2 outlet wired on 1 circuit) with 3x6 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in upto first outlet and 4 wire sq.mm.wire for the looped outlet in 25 mm dia heavy class uPVC/MS recessed / surface conduiting system including the cost of cutting / making good chases in brick work and including the cost of supplying and fixing modular grid plate mounted 220volt 16amp. 6 pin combined shuttered socket outlets alongwith 220 volt 16 amp.controlled switch of housed in GI boxes and including the cost of loop earthing with 4 sq.mm. FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires complete as per specifications and as required. | Nos. |  |  |  |  | 1 | 1 |  |  | 0 |  | 1 | 1 |  |  | 8
11 | Point wiring for 16 amp socket outlet points (One 16 Amp SSO with One 6 Amp SSO wired on 1 circuit) with 3x4 sq.mm. (P+N+E) FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires in 25mm dia heavy class recessed and / or surface uPVC electrical conduiting system including the cost of cutting / making good chases in brick work and including the cost of supplying and fixing modular grid plate mounted 220 volt 16amp. 6 pin combined shuttered socket outlets alongwith 220 volt 16 amp.controlled switch of housed in GI boxes and including the cost of loop earthing with 4 sq.mm. FRLS PVC insulated 660/1100 volt grade stranded copper conductor wires complete as per specifications and as required. | Nos. | [6 empty] | 4 |  | 0 |  |  |  | 1 |  | 10
|  | Nos. | 1 | 8 | 8 | 8 | 3 | 3 | 5 |  | 0 | 4 |  | 2 | 2 | 16 | 55
12 | Supplying and fixing class heavy MS surface conditing system including the cost of cutting/making good chases providing JB,Bends etc in brick work complete as per specificstion as required and as below ,For ELV system.
a | 25 mm dia | meter | 20 | 300 | 150 | 300 |  |  | 60 |  | 20 | 20 | 20 |  |  | 80 | 1479
b | 32 mm dia | meter | [14 empty] | 67
c | 40 mm dia | meter |  | 200 | 80 | 200 |  |  |  |  | 4 | 4 | 4 |  |  | 40 | 0
13 | Supplying & fixing 75mm x 75mm x 50 mm GI box with mould cord outlet complete with RJ 45 shuttered sockets as required for computer data point. | Nos. | 1 | 130 | 60 | 130 |  |  | 2 |  | 2 | 6 | 4 |  |  |  | 6
14 | Supply laying & termination of CAT - 6e cable on sutable cable tray all data cable termination Hub all so as required. ( Contractor will be responsible for structure cable approved for AT & T / Lapp ) | meter | 24 | 2500 | 1800 | 2500 |  |  | 60 |  | 24 | 24 | 24 |  |  | 96 | 1500
15 | Submain
1 | Wiring for submains with FRLS PVC insulated stranded copper conductor 660/1100 volt grade wires in surface/concealed conduit including cost of providing saddles etc. as required for surface conduiting and / or the cost of cutting and filling chases complete as per specifications as required and as below.
a | 2x10sq.mm in 40mm heavy class uPVC conduit and 1 Nos. 10sq.mm. FRLS PVC insulated stranded copper conductor 660/1100 volt grade wires for earthing. | meter | [8 empty] | 20 | [5 empty] | 25
b | 4x10sq.mm in 40mm heavy class uPVC conduit and 2 No. 10sq.mm. FRLS PVC insulated stranded copper conductor 660/1100 volt grade wires for earthing. | meter | [8 empty] | 8 | 16 | 24 |  |  |  | 251
c | 4x16sq.mm in 40mm heavy class uPVC conduit and 2 Nos. 10sq.mm. FRLS PVC insulated stranded copper conductor 660/1100 volt grade wires for earthing. | meter | [14 empty] | 35
2 | Supplying, laying, testing and commissioning of Heavy Duty GI perforated Tray with acceseries complite with supports ,earth continutiy ,in Open CC trench /Celling/Wall for cable laying as per standard including cost of Bracket supports ,grouting etc complite in all respect . clamping,dressing identification tags etc complete as per specifications, as required and as below.
a | 600 mm wide | meter | [14 empty] | 15
b | 450mm wide | meter | [14 empty] | 10
c | 300 mm wide | meter | [14 empty] | 25
d | 200 mm wide | meter | [14 empty] | 5
2 | Supplying, laying, testing and commissioning of 1100 volt grade armoured XPLE insulated and PVC sheathed aluminium conductor cable in cable on tray ensureing the minimum clearance between the cables as per standard including cost of clamping,dressing identification tags etc complete as per specifications, as required and as below.
a | 3.5 c 50sqmm | meter | [13 empty] | 0 | 25
b | 3.5 c 35 sqmm | meter | [14 empty] | 85
c | 3.5 c25 sqmm | meter | [14 empty] | 180
d | 3.5 c 16 sqmm | meter | [14 empty] | 280
e | 3.5 c 10 sqmm | meter | [14 empty] | 310
f | Control cable 5x 2.5 sqmm | meter | [14 empty] | 35
g | Control cable 12x 2.5 sqmm | meter | [14 empty] | 25
h | Control cable 19x 2.5 sqmm up to | meter | [14 empty] | 15
3 | Cable termination of XLPE cables as per above including the cost of criping heavy duty aluminium lugs double compression chrome plated brass glands insultaed tape and all requipte material for completion of termination complete as reuqired.
a | 3.5 c 50sqmm | Nos. | [13 empty] | 0 | 4
b | 3.5 c 35 sqmm | Nos. | [14 empty] | 10
c | 3.5 c25 sqmm | Nos. | [14 empty] | 18
d | 3.5 c 16 sqmm | Nos. | [14 empty] | 28
e | 3.5 c 10 sqmm | Nos. | [13 empty] | 0 | 30
f | Control cable 5x 2.5 sqmm | Nos. | [14 empty] | 4
g | Control cable 12x 2.5 sqmm | Nos. | [14 empty] | 6
h | Control cable 19x 2.5 sqmm up to | Nos. | [14 empty] | 2
Distribution board
1 | Supply, installation, testing and commissioning of factory fabricated and factory assembled TPN PPI ( Per Phase Isolation DBs ), sheet steel clad powder coated, wall / recess mounting dust and vermin (IP-42) ingress protection) proof double door Distribtion Boards fabricated from 16 SWG sheet steel provided with hinged gasketted door with padlocking facility and including suitably rated PVC insulated copper busbars with interconnections and neutral bar assemblies one per earthing terminals assembly etc , complete as requiredand as below. sample to be got approved by client (Note:- In all distribution boards / panels the control wiring shall be FRLS)
a | 12 way TPN as I/C 63Amps 4 pole MCCB , with 100/30 mA ELCB/RCCB 10 kA with 6/10/16/20 amps. SP 10 kA 'C' category MCB with thermal magnetic protective releases out goings. | Nos. | [14 empty] | 2
b | 8 way TPN as I/C 63Amps 4 pole MCCB , with 100/30 mA ELCB/RCCB 10 kA with 6/10/16/20 amps. SP 10 kA 'C' category MCB with thermal magnetic protective releases out goings. | Nos. | [14 empty] | 4
c | 6 way TPN as I/C 63Amps 4 pole MCCB , with 100/30 mA ELCB/RCCB 10 kA with 6/10/16/20 amps. SP 10 kA 'C' category MCB with thermal magnetic protective releases out goings. | Nos. | [13 empty] | 4 | 2
d | 8 way SPN DB I/C 1-40 amp. DP 10 kA MCB isolator incoming 100/30mA ELCB/ RCCB out going 6/16/20 amps. SP 10 kA 'C' category MCB with thermal magnetic protective releases out goings. | Nos. | [14 empty] | 4
2 | Deasign ,Supply and Installation of Main LT panel combined with AMF facility with Following details. | Nos | [14 empty] | 1
One (1) No. Digital Multifunction Meter suitable for measurement of voltage, currents, Power Factor, Frequency, Power & Energy with one set (3 Nos.) of CTs of ratio 1250/5A Class 0.5, 15VA.
a | 2 I/C ,1 Bus Cupler with 41nos Outging Main Panel .
b | JVVNL I/C with 1250 Ams 4P ACB ,DG incommer with 630ms 4P MCCB & Bus Coupler with 1250 Ams TP ACB .
c | Out going 100 Ams TP MCCB -5 No ,63Ams MCCB-22 nos,40 Ams TP MCCB 14nos.
3 | CAPACITOR (APFC) Panel, 200 kVAR | Nos | [14 empty] | 1
a | Bus Bars :
500 amps TP Al. Bus Bars 50kA fault level with coloured heat Shrinkable insulated sleeves. - 1 set
b | Outgoings :
3 Phase Intelligent Power factor correction relay with inbuilt metering features like:
5 Steps Relay
Total Current
Voltage
Power Factor
Current of each bank
1 No. Off delay timer for manual operation
a. | 1 Nos. 100 kVAR Sets, each comprising :
1 No. TP, MCCB of capacitor duty 50kA for 100kVAR Bank alongwith:
3P capacitor duty contactor with 2NO + 2NC auxiliary contacts for 100kVAR capacitor
A/M Selector switch
Illuminated ON/ OFF Push buttons
1 No. TP, MCCB of capacitor duty 50kA for 100kVAR Bank alongwith:
3P capacitor duty contactor with 2NO + 2NC auxiliary contacts for 100kVAR capacitor
b. | 1 Nos. 50 kVAR Sets, each comprising :
1 No. TP, MCCB of capacitor duty 50kA for 50kVAR Bank alongwith:
3P capacitor duty contactor with 2NO + 2NC auxiliary contacts for 50kVAR capacitor
A/M Selector switch
Illuminated ON/ OFF Push buttons
50kVAR Capacitor bank, MPP (Heavy duty) with 7% copper detuned reactor.
c. | 2 Nos. 20 kVAR Sets, each comprising :
1 No. TP, MCCB of capacitor duty 50kA for 20kVAR Bank alongwith:
3P capacitor duty contactor with 2NO + 2NC auxiliary contacts for 20kVAR capacitor
A/M Selector switch
Illuminated ON/ OFF Push buttons
20kVAR Capacitor bank, MPP (Heavy duty) with 7% copper detuned reactor.
d. | 1 No. 10 kVAR Set, each comprising :
1 No. TP, MCCB of capacitor duty 50kA for 10kVAR Bank alongwith:
3P capacitor duty contactor with 2NO + 2NC auxiliary contacts for 10kVAR capacitor
A/M Selector switch
Illuminated ON/ OFF Push buttons
10kVAR Capacitor bank, MPP (Heavy duty) with 7% copper detuned reactor.
In case of capacitor banks with de-tuned reactor, the operating voltage for capacitors shall be 525V minimum.
4 | Supply Installtion and Commissioning of 750 Kva ONAN Transfer | nos | [14 empty] | 1
| Excavation of Burried cable Trench | Mtr | [14 empty] | 2000
5 | Supply, loading, transportation unloading at site, storages at site, shifting from storage place to site of following sizes of 1.1kV grade XLPE insulated, Extruded PVC inner sheathed & overall FR-LSH PVC outer sheathed, Aluminium conductor, Armoured cables as per IS:7098 Part-I or amended upto date and as per specifications.
a | Laying of LT XLPE 3.5 x 300sqmm cable | Mtr | [14 empty] | 6000
6 | UPS - 20kVA
Supply of IGBT based micro processor controlled True On line double conversion 3 Phase input and 3 Phase output 20 kVA (0.9PF) UPS (N) consisting of following:
Each UPS module with integrated 100% rectifier + inverter.
Battery Circuit breaker for UPS module in CRCA housing with all required fixing accessories & hardware.
RS 485 BACnet/ Modbus protocol with UPS module for BMS Connectivity. All the informations to be provided to the BMS vendor at one point.
In-built static switch for bypass & inverter in UPS module.
In-built Manual maintenance bypass.
Interconnecting copper cabling (DC cabling) between UPS, Battery breaker & Batteries of required length and size.
UPS shall have a SNMP card for LAN/ WEB connectivity. The SNMP card shall have an inbuilt memory for event logging.
Sealed maintenance free batteries for 40 kVA UPS with 60mins. backup time on UPS module with inerconnectors, Rack and accessories. Rack shall have shrouds for safety from live battery terminals.
Suitable MS stand of 450mm high for UPS module duly painted.
RAM module with UPS and Cat 5 cable for RAM connectivity.
Charger Capacity 120%
UPS to have atleast two dry contacts for remote alarms.
a | 1x20 kVA UPS described above
1 | Earthing
| Supplying & Grounding Maintance free chemical filled earthing electrode 48mm x 3000mm including accessories & providing masonry enclosure with cover plate locking arrangement complete as required. | Nos. | [14 empty] | 8
a. | Supplying and laying earth conductors clamped to wall with suitable clamps saddles and fixing bolts / in ground including the cost of digging and back filling with bituminous protection complete as per IS 3043:1987 and as required.
| 25mm x 6mm GI strip | RM | [14 empty] | 290
G
1 | Lighting Fixtures & Fans
a | Supplying & fixing following box type LED light fixture complete with driver and LED lamp complete as required.2
| 1x22W surface mounting fixtures . | Nos. | 2 | 20 | 18 | 20 | 2 | 2 | 15 |  | 1 | 3 | 2 | 4 | 4 |  | 298
b | Supplying,Installation, testing and commissioing of 1200mm sweep ceiling fans including down rods of required length, canapy, suspending shackle, bladed electronic regulator etc. complete as required. | Nos. | 1 | 16 | 9 | 16 | 1 | 1 | 1 |  | 2 | 6 | 4 | 1 |  |  | 98
c | Supplying,Installation, testing and commissioning of 305mm dia exhaust fans including the cost of making hole in the wall making good, louvered shutter etc. complete as required. | Nos. |  |  |  |  | 1 | 1 |  |  |  |  | 1 | 1 |  |  | 20
d | Supplying & Installation of bulk head fitting with glass receptacle, wire guard lamp holder, lamp including connection complete as required. | Nos. | [14 empty] | 5
| TOTAL |  |  |  | 2140
GST 18%
GRAND TOTAL

## C.C. ROAD
CIVIL WORK FOR "CONSTRUCTION OF LNMIIT MESS BUILDING "
BOQ CIVIL WORKS -MESS BUILDING
S. No. | ITEM DESCRIPTION | QUANTITY | UNIT | RATE | AMOUNT
C.C. ROAD
| Providing and laying lean cement concrete 1:4:8 in Sub- base over a prepared sub-grade with coarse and fine aggregate conforming to IS: 383, the size of coarse aggregate not exceeding 25 mm, aggregate cement ratio not to exceed 15:1, aggregate gradation after blending to be as per table 600-1, cement content not to be less than 150 kg/ cum, optimum moisture content to be determined during trial length construction, concrete strength not to be less than 10 Mpa at 7 days, mixed in a batching plant, transported to site, laid with a paver with electronic sensor, compacting with 8-10 tonnes vibratory roller, finishing and curing complete as per clause 601, 112 of MoRT&H specification including all material, labour, machinery, lighting, guarding and maintenance of diversion. | 152.2 | Cu.mt. |  | 0
17.21 | Kerb Stones of 1200x300x150, 1000x450x150, 1000x600x150, 600x300x150 size (M-30)
| Providing and Laying cement concrete Kerb Stones of different sizes in M-30 grade (Manufactured with fully mechanised dry cast process with forced action mixer whose arms revolve along the main axis and rotate about its own axis also, having humidity sensor for moisture control of w/c ratio in concrete mix. Manufactured with steel moulds (Milled and manufactured in CSI diamond or CSI Nitro process for accuracy) on steel base plate of min 16 mm thick; Having Vibration and pressing action both together with the help of multiple synchronised vibrators. Power of hydraulic station should be minimum 50KW for compaction and cured in controlled chambers having humidity control and automated air circulation system) in position to the required line, level and curvature jointed with cement mortar 1:3 (1 Cement : 3 Coarse sand) including making of joints, drainage opening wherever required. | 10 | Cum |  | 0
| TOTAL |  |  |  | #REF!
GST 18%
GRAND TOTAL

## FAS & PA syt.
CONVENTIONAL FIRE ALARM SYSTEM ESTIMATE
PROPOSED NEW MESS, LNMIIT, JAIPUR
SR. NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
FIRE DETECTION AND ALARM SYSTEM - ANALOG ADDRESSABLE SYSTEM
Design, Supply, installation, testing & commissioning of Fire Detection & Alarm system as per local fire norms & NBC/ NFPA Codes:
1 | SITC Addressible Optical type Smoke Detector with mounting base, LED etc. as required. | 128 | NOS
2 | SITC of Rate of Rise cum fixed temperature thermister type Heat Detectors with LED, mounting base etc. as required. | RO | NOS
3 | SITC of Response Indicator for detectors as required | 5 | NOS
4 | SITC of Addressible type Manual call point complete with Glass, hammer and chain etc. as required. | 6 | NOS
5 | Providing, fixing, testing and commissioning of electronic hooters with LMT (hooters shall also be able to work as public address system sounders) housed in sheet steel / Polymer housing suitable for wall / ceiling and surface / recess mounting including making connections with wires complete in all respects and as per specifications. | 6 | NOS
6 | SITC of wall / floor type following zone (each zone accessing minimum 20 units (detectors/ devices ) Addressible Type microprocessor based with LCD display main control panel/ floor panel fabricated from 16 SWG CRCA sheet steel sealed maintenance free (SMF) batteries of min2X7AH of 12 V or as required.
6.1 | 8 zone | 1 | NOS
7 | Supply & laying of LPCB certified 2c x 1.5 sq.mm Fire Survival/ Resistance Armoured cable (600/ 1000V) with class-2 Copper conductor having halogen free ceramified silicon rubber insulation as per BS EN 50363 and low smoke zero halogen (LSZH) inner & outer sheath. Should comply to EN 61034-2 & EN 60754-1. LPCB-FPC certificate to be submitted. The cables should meet fire performance circuit integrity test as per BS EN 50200: PH-120. Outer sheath should be in red colour with Anti-rodent & LSZH properties, 950°C rating for three hours for fire alarm system. (with fixing arrangement & termination.) | 1400 | MTR
8 | Supply, Laying 25 mm dia HEAVY GUAGE MS Conduit | 1200 | MTR
9 | Carbon dioxide (CO2) type fire extinguisher (conforming to IS 2878) with cylinders fully charged of capacity 9.0 Kg.) | 6 | Nos
GRAND TOTAL COST IN Rs.
13 | INTIGRATED DIGITAL VOICE EVACUATION AND DIGITAL 2 WAY COMMUNICATION FIRE FIGHTER SYSTEM
Supply, installing, testing and commissioning of Integrated 8 channel (FOR 8 DIFFERENT TYPE OF MESSAGES TO GET RELAYED SIMULTANEOUSLY) Digital Voice Evacuation and 2 way Communication Fire Fighters System capable to supervise all the speaker circuits, with required number of zone control as given below and accessories required to complete the system. The equipment shall be of same make as panel. DVC shall offer minimum one fire man's telephone circuit & one speaker's circuit. DVC shall be with in-built digital microphone, fire man's telephone hand set & PA Zone control.
| DVC with 4 zone control | 1 | No
Notes: | Networkable DVC with in-built features like:
a. | In-built 'PA' Zone control
b. | In-built 'PA' Microphone
c. | In-built Fire Main's telephone hand set for 2 way communications.
d. | 'Aux'/ IPAD/ EPABX Input ports for music
e. | Facility to control all PA zones
f. | Facility to relay pre-corded massages
g. | DVC to give out one Fire Man's telephone riser & 32 Nos. Digital Amplifiers loop.
14 | DIGITAL AMPLIFIERS
Supply, installing, testing and commissioning of Addressable & fully supervised DIGITAL AMPLIFIERS with minimum Wattage as given below with 70.7 VRMS. The Digital Amplifiers shall have inbuilt minimum of 4 Speakers Zone Circuits and minimum 1 Fire Fighters communication. The Amplifiers shall be stand alone with its own battery backup incase of Main fire Alarm panel/ Digital Voice Panel failure and the Digital Amplifiers shall still be in position to carry out Voice Evacuation.
a. | 500 Watts | 2 | No
b. | 100 Watts | 0 | No
a. Amplifier shall sit on Amplifier loop
b. Amplifier shall have minimum in-built four PA speaker zones
c. Amplifier shall have a fire man's telephone riser
d. Amplifier shall support 2 way communication for fire man
e. Telephone hand set for 2 way communication to be ordered seperately as may be required.
15
16 | WALL MOUNTED SPEAKERS
| Supply, installing, testing and commissioning of Fire panel supervised 78db-90db Wall Mounted Speakers as specified & same make as of panel. Speakers shall be 2 Watt with multi taps of 0.25W, 0.5W, 1W and 2W. | 14 | No
17 | FIRE FIGHTERS TELEPHONE JACK
| Supply, installing, testing and commissioning of 2 way communication Fire Fighter's Telephone Jack | 6 | No
18 | FIRE FIGHTERS HANDSET
| Supply, installing, testing and commissioning of 2 way communication Fire Fighter's Handset | 2 | No
| TOTAL |  |  |  | #REF!
GST 18%
GRAND TOTAL

## FF
FIRE FIGHTING WORK
S. No. | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.)
HYDRANT SYSTEM
13 | Supplying and fixing Gun metal single headed Internal / external yard hydrant valve with 1 No. 63 mm dia instantaneous Gun metal coupling and cast iron wheel, ISI marked, conforming to IS 5290 (type A) with blank Gunmetal cap and chain as required. | Each | 31
14 | Supplying and fixing of Hose Cabinet of size 750 mm x 600 mm x 250 mm made of 1.6 mm thick MS sheet with 6 mm thick glazed glass doors including necessary locking arrangement suitable to accommodate external hydrant with butterfly valve, 2 Nos 15 Mtr. Long Hose pipe, 1 No. branch pipe, mounted on wall OR raised brick platform & duly painted with post office red externally and white internally with synthetic enamel paint complete in all respect, for external hydrant, as required. | Each | 10
15 | Supplying and fixing of Hose Cabinet of size 2100 mm x 900 mm x 715 mm made of 1.6 mm thick MS sheet with 6 mm thick glazed glass doors including necessary locking arrangement suitable to accommodate Internal hydrant with butterfly valve, 2 Nos 15 Mtr. Long Hose pipe, 1 No. branch pipe, first aid hose reel drum etc. & mounted on wall OR raised brick platform & duly painted with post office red externally and white internally with synthetic enamel paint complete in all respect, for external hydrant, as required. | Each | 21
16 | Supplying and fixing Fire Brigade Connection of CI body with Gun Metal male instantaneous inlet couplings complete with cap and chain as required for 150mm dia MS pipe connection, conforming to IS 904 as required of following way :
a) | 2 Way (for Drawout ) | Each | 1
b) | 4 Way (for Inlet) | Each | 1
17 | Providing and fixing of 4 way suction coupling for fire brigade withdrawal of water from fire tank with 150mm dia pipe and foot valve. | Each | 1
18 | Supplying and fixing 63 mm dia, 15 mtr. Long RRL hose pipe with 63 mm dia male and female Gun metal couplings duly binded with GI wire, rivets etc. conforming to IS 636 (type-A) as required. | Each | 62
19 | Supplying & fixing 63 mm dia Gun metal branch pipe with 20 mm (nominal internal diameter) size nozzle confoming to IS 903, suitable for instantaneous connection to interconnect hose pipe coupling as required | Each | 31
20 | Providing & fixing 100mm dia bourden type, Stainless steel dial type pressure Gauge (0 - 16 Kg ) range, 3 / 8 " BSP bottom entry on Pump Delivery Line complete with Ball valve | Each | 15
21 | Supplying and fixing first -Aid hose reel wall mounted swinging type with MS construction spray painted in post office Red, conforming to IS 884 with upto date amendments, complete with the following as required.(A) 30 m long 20 mm (nominal internal) dia water hose Thermoplastic (Textile reinforced) Type -2 as per IS: 12585 (B)20 mm (nominal internal) dia gun metal globe valve & nozzle.(C)Drum and brackets for fixing the equipments on wall.(D) Connections from riser with 40 mm dia stop valve (gun metal) & M.S. pipe | Each | 21
22 | Supply & Fixing of Fire Man's Axe with heavy Insulated rubber tested up to 20 KV and confirming to IS ;926 | Each | 31
23 | Providing, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 / 1239 for hydrent and sprinkler applications including fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. fixing the pipe on the wall/ceiling with suitable clamps and including painting of two coats of Red Oxide , painting with two or more coats of synthetic enamel paint of Post office red shade complete as required.The installation includes all civil openings ,breakages and making good the same.
24 | 25 mm dia | Mtrs. | 2500
ii | 32 mm dia | Mtrs. | 1500
iii | 40 mm dia | Mtrs. | 600
iv | 50 mm dia | Mtrs. | 350
v | 65 mm dia | Mtrs. | 425
vi | 80 mm dia | Mtrs. | 250
vii | 100 mm dia | Mtrs. | 350
viii | 150 mm dia | Mtrs. | 400
ix | 200 mm dia, 6.0 mm thick | Mtrs. | 20
x | 250 mm dia, 6.35 mm thick | Mtr. | 20
25 | Providing, laying, testing & Commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 and 1239 for hydrent and sprinkler underground rings including all accessories such as screwed/ welded flanges, tees, reducers etc. Conforming to IS : 1239/3589 complete including , welding, jointing with compressed asbestos gaskets, nuts, bolts etc. as required. with cleaning,wrapping and coating of the pipe with 4 mm thick tar based plymaric corrosion protection tape or equivalent including applying uniform coat of cold pipekot primer as per IS; 10221 for protection against corrsion suitable for all kind of soil at 1.0 M depth including excavation and making good the same as required at site .
i | 80 mm dia | Mtrs. | 25
ii | 150 mm dia | Mtrs. | 500
26 | Providing, installation, testing and commissioning of dual plate non-return valve of following sizes confirming to IS:5312 complete with rubber gasket, G I bolts, nuts, washers etc. as required.
i | 80 mm dia | Each | 2
ii | 100 mm dia | Each | QR
iii | 150 mm dia | Each | 4
iv | 200 mm dia | Each | 1
27 | Supplying, fixing, testing commissioning of butterfly valve PN 1.6, with Bronze/ Gunmetal seat duly ISI marked complete with Nuts, Bolts, washers, gaskets, conforming to IS 13095, of following sizes as required.
a) | 80 mm dia | Each | 1
b) | 100 mm dia | Each | 1
c) | 150 mm dia | Each | 21
28 | Providing, installation, testing and commissioning of Brass ball valves of following sizes as required.
| 25 mm dia. | Each | QR
| 32 mm dia. | Each | 10
| 40 mm dia | Each | 10
| 50 mm dia | Each | 10
29 | Providing, fixing, testing & commissioning of 15 mm dia size ,quartzoid bulb sprinkler heads suitable for 68 degree centigrade rating of the following type :
i | Pendant type | Each | 1490
ii | Upright type | Each | 200
iii | Sidewall Sprinklers (ordinary) | Each | 20
30 | Providing & fixing testing & commissioning of installation control valve of cast iron body and brass/bronze working parts comprising of water motor alarm, bronze seat clapper, and clapper arm, hydraulically driven mechanical gong bell to sound continous alarm when the wet riser/Sprinkler system activates, pressure gauges, emergency releases, strainer, pressure switch, cock valve complete with drain valve and bypass, test control box, ball valves, MS pipe of required size, flanges, orifice plate, gasket etc. of size 150 mm dia as required. | Each | 1
TOTAL OF HYDRANT SYSTEM
FIRE EXTINGUISHERS | FIRE EXTINGUISHERS
31 | Supply & Fixing ISI marked ( IS : 15683 ) Poratable Fire Exitnguisher,Trolley mounted Mech. Foam type capacity 09 ltrs with gun‐metal cap and nozzle and complete respects in all respects including initial fill and wall suspension. | Each | 6
32 | Supply & Fixing ISI marked ( IS : 15683 ) Portable Fire Exitnguisher, ABC type,finished externally with red enamel paint, complete in all respects including initial fill and wall suspension of following capacity.
| 6 kg | Each | 35
33 | Supply & Fixing ISI marked ( IS : 15683 ) Portable fire Extinguisher, Carbon‐dioxide type flat base including valve, discharge hose of not less than 10 mm dia. min. 600 mm long & complete in all respects including initial fill with C02 gas confirming to IS:307‐1966 filled to a filling ratio of not more than 0.667and wall suspension bracket. Capacity 4.5 Kg. | Each | 10
TOTAL OF FIRE EXTINGUISHERS
TOTAL ESTIMATE
GST 18 %
GRAND TOTAL

## Biometric
BIOMETRIC CUM SMART CARD ELECTRONIC READER (ECR) with OPTICAL FACE READER SENSOR (WALL MOUNTED)
SR. NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
1 | Highly reliable Electronic Card Reader machine should be biometric finger scanner having contactless smart card sensing facility with finger only, card only, card + finger, Finger+ PIN etc. The fingerprint scanner should be scratch proof type. | nos | 20
Clear Audio-visual verification Identifiable beep sound for successful/ Unauthorized/ Already Punched (successive punch).
Identification speed of punch: less than 1 second.
Clear audio-visual verification Identifiable beep sound for successful/ Unauthorized/Already
Punched/(successive punch)
Face recognisation Template storage capacity: no of templates— minimum 5000 per machine(1:N)
Log capacity capacity at least 50,0000
Network interface by TCP/ IP or RS485 Wiegand input/output configurable up to 64 bits
Internal relay for direct lock interface (standalone control mode)
TOTAL ESTIMATE
GST 18 %
GRAND TOTAL

## Wifi & Lan
Data Network & WIFI System
SR. NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
Data Network & Wifi System
NETWORK COMPONENTS
NETWORK ETHERNET SWITCH:
Simple Network Management Protocol (SNMP)
Network Cables :- To Establish the Connectivity between Field Switches to Existing Central Switches & Camera,Biometry System to Switches, UTP CAT-6E level cable will be installed, if distance between the above Object is less than 90 mtr. If the distance exceeds beyond 90 mtr. Then Single Mode OFC Cable will be required to install .
| All user outlets will be identically wired with UTP Cabling system conforming to Category 6E UTP Cabling system TIA/ EIA 568-B.1 standards. | 4 | Nos
Networks Supported :- 10 / 100 Ethernet, 155 Mbps ATM, 1000 Mbps IEEE 802.3ab Ethernet, and proposed Cat 6 Gigabit Ethernet
WiFi SYSTEM ( For Gr.First & Second Floor) with 50 ,First Floor 500 & second Floor 500 users.
1 | )The Router should be modular in architecture with multicore processor. Router should have 4 nos. of 10/100/1000
2 | Base-T ports out of which 4 nos. should have SFP based ports option. Router should have 1x RJ-45 and 1xUSB console port.
3 | )Router should have 1:1 redundant internal and field replaceable power supply
4 | ) Router should have at least 2 open slots for additional LAN/ WAN modules other then above asked ports
5 | 4)The router should have minimum 8GB DRAM active and 8 GB Compact Flash from day one
6 | 5) Router should have a minimum throughput of 500 Mbps or more with all services enabled
TOTAL ESTIMATE
GST 18 %
GRAND TOTAL

## CCTV
CCTV SYSTEM
SR. NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
CCTV SYSTEM
Purpose of the system is to provide surveillance to the entire premises .at remote places ,& Localy.
All indoor and outdoor cameras are IP based POE or POE+
To be connected Existing Video recorder and Redundant Data Base server .
True day/ night functionality providing vivid color images by day and clear black-and-white images at night with ICR.
Be available to record streaming video or snapshot images to a SD Card in case of Event/ Alarm scenario.
The cameras should provide micro-SD card slot for recording when there is an event (Alarm, Motion detection, Network failure detection) or scheduling.
The cameras should have a provision to provide a warning message through relay output/ FTP/ Email/ HTTP, upload an image through FTP/ Email or record video to a micro-SD card/ network recorder upon motion detection/ network failure disconnection.
TYPES OF IP CAMERA
| 3 MP MFZ Dome Camera: | 2 | Nos
a) Type :- Nework IR Varifocal Dome Camera
b)Resolution (No of Pixels) :-3MP (1920x1080)
c)Lens :- Motorised Focused and Zoomed
d) User Access :- Maximum 10
e)Net Work :-RJ45 (10 BaseT/100 BaseTX)
f) Input Power :- 12v DC /PoE
g) Event Linkage :- Event notification using Email and MicroSD card
| 3MP DOME FIXED LENSE Camera: | 4 | Nos
a) Type :- Nework IR Varifocal Bullet Camera
b)Resolution (No of Pixels) :-3MP (1920x1080)
c)Lens :-
d)
e)Net Work :-RJ45 (10 BaseT/100 BaseTX)
f) Input Power :- 12v DC /PoE
g) Event Linkage :- Event notification using Email and MicroSD card
VIDEO MANAGEMENT SYSTEM ( VMS)
1)The Video Management System (VMS) shall control multiple sources of video surveillance subsystems in a facility to collect, manage and present video in a clear and concise manner.
2) VMS shall provide a single graphical user interface (GUI) to monitor, control and administer digital video surveillance equipment from multiple systems and platforms.
3) VMS shall be based onExisting server client architecture with Existing server & controller containing a database of all network-connected cameras, integrated components and their configurations; and Workstations that will render video and act as a main user/ machine interface.
4) VMS shall include a fully scalable enterprise-class media management system to enable simultaneous live monitoring from multiple stations and be configurable for storage both on and off site.
5)VMS software shall be configured to store and to view images captured by one camera or numerous cameras and monitor connections across an unlimited number of servers.
6) Capable of managing the integration with multiple digital IP cameras through compatible recording devices.
| Complite with Cat6E POE cables ,installation hardwares ,cable laying inside conduit etc. | 560 | MTR
TOTAL ESTIMATE
GST 18 %
GRAND TOTAL

## HARDWARE
New Mess, LNMIIT, JAIPUR.
SR.NO | PRODUCT DESCRIPTION | PRODUCT CODE & SIZE | IMAGE | WARRANTY
EBCO
1 | Mortise Door Lock Set - Ebco (One side key, SS Plate) For Toilets | MDLS-EKL |  | 5 YRS
2 | Glass Door Handles - H | H-GDH-3275 |  | 5 YRS
3 | Door Closer 201 | DC 201 |  | 5 YRS
4 | Turn Latch for Handicap Toilet | TL-1 54mm x 41mm |  | 5 YRS
5 | Sliding Window Latch Eco (With Child Lock) | SWL 2 |  | 5 YRS
HETTICH
1 | SS 304 (4’’ x 3’’ x 3’’) without screws - Bulk pack |  |  | 5 YRS
2 | Fixing Screw 4.8 X 31 SS for Butt Hinge
3 | ProLock 1 HH 2650 Handle + Handle set SS |  |  | 5 YRS
4 | Round PZ Escutcheon 1 |  |  | 5 YRS
5 | HBS 31 FSL: Sash Lock DIN Left/Right CTC 72 & Backset 55 |  |  | 5 YRS
6 | HTCL 60: One side key and one side knob 60 mm, for max door thickness - 40 mm |  |  | 5 YRS
7 | HPH 2310: Back to Back Pull Handles Dia. 25mm, CTC Length 400, SS Finish |  |  | 5 YRS
8 | HDV 2: Door viewer 140° view (for door thick-35-55mm) |  |  | 5 YRS
9 | HDS 44: Door Stopper |  |  | 5 YRS
DORSET
1 | Tower Bolt | TS-610 150mm |  | 1 YEAR
2 | Door Stopper (Hanging Type) | DSHT |  | 1 YEAR
HAFELE
1 | BALL BEARING BUTT HINGE,SS304,SSS,4"X3"X3MM-2 BB,SQUARE CORNER,WITH TIMBER DOOR SCREW, SSM | 926.32.160 |  | 1 YEAR
2 | Mortise Cylinder Lockcase 55Mm Backset, 72Mm Center, 24Mm Square Forend, SSM | 911.02.164 |  | 1 YEAR
3 | Euro Profile Thumb Turn Cylinder With Key, 31.5+31.5 = 63Mm, Non-Masterkeyed, SN | 916.96.306 |  | 1 YEAR
4 | Hollow D Lever Handle On Rose With Europrofile Cylinder Escutcheon, SSM | 903.92.586 |  | 1 YEAR
|  | OR |  | 1 YEAR
5 | Hollow L Lever Handle On Rose With Europrofile Cylinder Escutcheon , SSM | 903.92.556 |  | 1 YEAR
|  | OR |  | 1 YEAR
6 | Hollow U Lever Handle On Rose With Euro Profile Cylinder Escutcheon, SSM | 903.92.596 |  | 1 YEAR
|  | OR |  | 1 YEAR
7 | Basta, Hollow SS Lever Handle On Rose With Euro Profile Cylinder Escutcheon | 903.99.058 |  | 1 YEAR
|  | OR |  | 1 YEAR
8 | Solid Lever Handle On Round Rose And Euro Profile Cylinder Escutcheon - SS 316 | 903.99.217 |  | 1 YEAR
9 | Floor Mounted Door Stopper, Half Round, SSM | 937.55.140 |  | 1 YEAR

## Civil Makes
MESS : INTERIOR & CIVIL WORKS LIST OF MAKES
Sr. No. | Material / Item | Approved Makes
Make
EXCAVATION
1 | Anti-Termite Pesticides - (Imidacloprid)
Bayer
PPC & RCC WORK
2 | Cement OPC/ PPC | Ultratech
Wonder
3 | Cement - White
J.K.White
Birla White
4 | Admixture for Concrete
SIKA
Fosroc
5 | Reinforcement Steel: Main Producers only
TATA
(TISCO)
JSPL
6 | Ready mix Cement Concrete
Ultratech
Nuvoco
9 | Concrete Curing Compound
Fosroc
Sika
10 | Core cutting
Hilti
Wurth
11 | AAC block
Ultratech,
JK Laxmi
Megicrete
12 | Hollow core wall panel
Aerocon
Everest
DOORS & WINDOWS WORK
13 | Floor spring, door closer & door automation
Dormakaba
Hafele
14 | Door lock
Dormakaba
Hafele
15 | SS 304 Door Hardware for D/W (other than FIO spring, Closer, Locks)
Dormakaba
Hafele
16 | Aluminium extrusions and section
Jindal
Hindalco
17 | toughened glass
Saint Gobain
Modi Guard (Gujarat Guardian)
18 | Metal Fire rated Doors
Shakti Hormann
Navair
19 | Fire Rated Hardware & system
Dormakaba
Assa Abloy (Yale)
Hafele
Hormonn
20 | Fire Seal, Fire smoke Seal
3M
Hilti
Dormakaba
21 | Fire rated Glass
Vetrotech (Saint-Gobain)
Pyroguard
22 | Modular Toilet Cubical
Greenlam
Merino
Fundermax
23 | Laminates
Greenlam
Century
24 | Urinal Partition made out of laminated compact sheet
Greenlam
Merino
25 | Polysulphide Sealant/ PU sealant
Pidilite
Fosroc
Sika
Mapei
26 | Clear Toughened Glass
SaintGobain
Modiguard (Gujarat Guardian)
27 | Silicone Sealant
Wacker
Mapei
28 | Mirrors (superior quality crystal clear)
Saint Gobain
Modi Guard (Gujarat Guardian)
29 | Polyester Powder coating/ PVDF Coating
Jotun
Akzo nobel (Interpon)
Orbit
30 | Structural Silicon sealant, Pre pigmented Weather Silicone
Dow Corning
Momentive (GE)
Tremco
31 | Acoustic Seal / Door seal
32 | Wood Adhesive
Fevicol
Araldite
3M Fasara film
WATER PROOFING WORK
33 | Water Proofing compound
Fosroc
Sika
34 | Water proofing membrane (PVC/ HDPE)/ Water proofing coating (PU/ Polyurea/ Acrylic/ Elastomeric cementitious)
Fosroc
SIKA
35 | Water Stops - Hydrophilic Swellable rubber strip (Not bentonite type)
Pidilite
Fosroc
SIKA
FLOORING WORK
36 | Vitrified Tiles (Full body)
RAK
Restile
Kajaria (Eternity)
Somany
Jonnson
Nitco
37 | Tiles/ Stone fixing Adhesive (Only High performance, polymer modified, non- slip adhesive)
Ardex Endura
MYK- Latricrete
Saint Gobain- Webar
Roff
38 | Epoxy Grout/ Cementitious Grout for Flooring
Ardex Endura
MYK- Latricrete
Saint Gobain- Webar
Roff
39 | Stone sealer
MYK- Latricrete
40 | Raised/ false access flooring system
| Unitile Lindner Unifloor Tankaria Tankaria AET | Unitile
Lindner
Unifloor
Tankaria
AET
41 | Solid surface (Corian)
Dupont
| Dupont,Neonnex,LG,Staron-Samsung,Hanex,Durlax | Neonnex
LG
Staron-Samsung
Hanex
Durlax
42 | Engineered Marble
HR jhonson
kallinga stone
Nitco
43 | Vinyl Flooring
Tarkett
Merino
Squarefoot
METAL WORK
44 | Stainless Steel
SAIL
Jindal
Tata
45 | Structure Steel & Hollow Section - Producers only
SAIL
TATA (TISCO)
Jindal steel & Power (JSPL)
Apollo tube
46 | Aluminium sections and plate
| Hindalco Jindal Banco Bhoruka Global | Hindalco
Jindal
47 | Anchor Fastener, Rebar, Chemical/ Mechanical fastener, Expandable fasteners
Hilti
48 | Non shrink cementious precision (anchoring) grout | GYPSUM
Fosroc
Sika
Mapei
Pidilite
BASF
PAINTING WORK
49 | White cement based putty
Birla
Asian
50 | Paint - Plastic Emulsion (Internal)
Asian
Berger Paints
51 | Paint - Synthetic Enamel
Asian
Berger
52 | Paint - Acrylic Emulsion (Exterior)
Asian Paints
Berger
53 | Paint - Texture Paints
Asian (Nova Colour)
54 | Paint - PU & epoxy paint and primer
Asian
Berger
CEILING & WALL PANELLING WORK
55 | Gypsum ceiling system (plain/ perforated),
Saint Gobain
USG Boral
Knauf Danoline
Armstrong
56 | Dry wall Gypsum partition system, Gypsum wall paneling
Saint Gobain
USG Boral
Knauf Danoline
57 | Aluminium Metal Ceilings (Baffle, plank and Open cell ceiling)
Armstrong
Hunter Douglas
Bollard
58 | Plywood
Greenply
Century
Merino
59 | Acoustic panel
Silence Panel
Anutone
Saint Gobain
Armstrong
60 | Cement Fiber Board/ Cement bonded particle board
Everest
NCL Industries (Bison Panel)
Shera Board
Visaka Industries (V- Next)
Century (Zykron)
61 | GI suspended ceiling grid system & Close/ C stud framing system
Saint Gobain
USG Boral
Knauf Danoline
62 | Access panel in False ceiling system
Saint Gobain
USG Boral
Knauf Danoline
63 | Rock wool/ Glass wool Insulation
UP Twiga
Roxul Rockwool India
Lloyd
Siderise
Wall Tile
64 | Vitrified Tile | Kajaria
Somany
Restile
Johnson
65 | Quads Porcelain Tiles
Johnson
66 | Reflective Tap
3M
67 | ACP
Aluco Bond
Aludecor
Alubond
Aludecor
68 | PUF Panel
Kingspan
Tata BlueScope
Epack
Everest
69 | Galvalume Sheet
JSW
Tata BlueScope
70 | Barbed wire fencing
Tata
Jindal

## Sanitary Fixture Schedule
ANNEXURE_ SANITARY FIXTURE B.O.Q
Sr. No. | Item Name | Code | Finish | Description | Make | Image
1 | WASH BASIN | k-2075IN-1-0 | White | Serif™ 56.4 cm oval self-rimming bathroom sink with glazed underside | KOHLER | #VALUE!
2 | Complementary Grid Drain | K-20746IN-CP | White | Complementary™ Bathroom sink grid drain without overflow | KOHLER | #VALUE!
3 | Fore Arc Pillar Tap | K-27486IN-4-CP | Polished Chrome | Fore Arc™ Single-handle bathroom sink faucet, cold only, 16.5 lpm | KOHLER | #VALUE!
4 | Complementary Angle Valve | K-80158IN-9-AF | Vibrant French Gold | Complementary™ Angle supply stop valve | KOHLER | #VALUE!
KOHLER
5 | Reach ECOWHB + Reach QC Slim Seat | 30438IN-0 | White | Reach Eco wall hung toilet bundle in White | KOHLER | #VALUE!
6 | Evo Flush frameless Mech In Wal Tank | K-33926IN-M-0 | White | Evo Flush™ In-wall tank without frame | KOHLER | #VALUE!
7 | Riviera IWT Mech -CP Dual-flush faceplate | K-28476IN-M-CP | Polished Chrome | Riviera™ Dual-flush faceplate | KOHLER | #VALUE!
8 | Span Round Rear Inlet | K-26475IN-ER-0 | White | Span™ Wash-down half-stall 0.5 – 3.8 lpf urinal, rear spud K-26475IN-ER-0 | KOHLER
9 | Paper holder/ Tissue Holder | K-5633IN-CP | Polished Chrome | Complementary™ Covered toilet paper holder | KOHLER
10 | Bottle Trap 350 MM | K-75823IN-CP | Polished Chrome | Complementary™ 32 mm x 32 mm bottle trap | KOHLER
11 | July 1 WAY BIB COCK | K-16093IN-4-CP | Polished Chrome | July™ 1-way bib tap | KOHLER
12 | Patio Urinal Sensor | 24199IN-C01-CP | Chrome | Patio™ Urinal Sensor | KOHLER
13 | SS TAG HOLDER ON DOOR

## Plumbing Makes
LIST OF PREFERED MAKE FOR PLUMBING WORKS
Sl. No. | Materials | Approved Makes
1 | Sanitary Fixtures | Jaquar, Kohler
2 | Conceled Cistern | Geberit, Kohler,
3 | Sink | Jayna
4 | WC Connector | Geberit, Kohler
5 | Auto Urinal Flush System | Jaquar, Kohler
6 | Hand Drier | Grohe, Kohler
7 | CP Fittings | Jaquar, Kohler
8 | Gl Pipe (IS:1239, Part-I) | Tata, Jindal (Hissar) SAIL
9 | Gl Fittings (IS:1239, Part-Ll) | Zoloto
10 | Gl Pipe Sealent | Henkel - LOCTITE 55, Superbond, Sealtite
11 | GI/MS Pipe Protection Wrapping & Coating | IWL – Pypkote, Rustech – Coatek
12 | TEFLON TAPE | As Per Approval Of Engineer In Charge
13 | Floor Drain Fixture & Channel Gratings | Kessel, ACO, Viega
14 | Anchor Fastener | HILTI, FISHER
15 | Supporting Material For Piping | HILTI, FISHER
16 | UPVC Pressure Pipes And Fittings (IS:4985) | Supreme, Astral,Finolex
17 | CPVC Pipes And Fittings | Supreme, Astral,Finolex
18 | RCC Pipe | Indian Hume Pipe,
19 | HDPE Pipe | Supreme, Vectus, SFMC
20 | Pre-Fabricated HDPE Manholes | Supreme, Vectus, Astral
21 | Centrifugal Cast Iron Hubless Pipe IS: 15905 | SKF, NECO, HEPCO, RPMF
22 | CI LA Pipes And Fittings (IS:1536) | Electro Steel Calcutta, NECO, Jindal Supreme
23 | Manhole Covers & Frames | Neco, Raj Iron Foundry Agra, Kartar, GMGR, SKF
24 | GM / Forged Brass Ball Valves | Danfoss,Honeywell
25 | Sluice Valves | Kirloskar, Zoloto,
26 | Motorized Valve | Honeywell, Zoloto, L & T
27 | Butterfly Valve | Zoloto, Kirloskar,
28 | Check Valve – Wafertype | Advance, Zoloto, Kirloskar,
29 | Check Valve - Dual Plate | Zoloto, Kirloskar,
30 | Check Valve Forged Screwed | Zoloto, Kirloskar,
31 | Cast Iron Non Return Valve | Zoloto, Kirloskar,
32 | NRV - Ball Type - Sewage Application | Zoloto, Kirloskar,
33 | Pressure Reducing Valve | Honey Well, Danfoss,
34 | Three Way / Two Way Motorized Valve | Honey Well, Danfoss,
35 | Air Release Valve | Danfoss, Kirloskar,
36 | Ball Float Valve | Danfoss, Kirloskar,
37 | Air Vent | , Honeywell,
38 | Y Strainer CI | Emerald, Sant, SKS,
39 | Backflow Preventer | Supreme, Kessel, ACO
40 | Drinking Water Cooler | Blue Star, Voltas
41 | Submersible Sump Pump | Grundfos, KSB, Xylem
42 | Hydro Pneumatic Transfer Pump | Grundfos, KSB, Xylem
43 | Mechanical Seal | Burgmann, Sealol, Leakpack
44 | Anti-Vibration Mounting & Flexible Connections | Resistoflex, Dunlop, Flexionics
45 | Pressure Gauge | FIEBIG, H-GURU, Emerald
46 | Water Meter (Mechanical Type) | Kent, Capstan, Kranti
47 | Electronic Flow Meter | Rockwin, Peltek, Manas Microsystems
48 | Level Controller & Indicator (Water)/Pressure Transmitter | Technika, Minilec, Elegent Controls
49 | Hot Water Pipe Insulation | Armacell /Kaiflex/ Armaflex/ Eurobatex (Italy)
50 | Welding Rods | Advani, ADOR, Esab
51 | Fire Sealant | 3 M, Hilti,
52 | Temperature Sensor/ Gauge | Forbes Marshall, Danfoss, Wika
53 | Water Treatment Vessel | Astral, Pentair
54 | Ultra Violet Water Purifier (WTP / STP) | Alfa UV - Mumbai / Eureka Forbes / Pentair
55 | Dosing Pumps | Fluid Controls, Grundfos
56 | FILTERS | GOPANI/THERMAX
57 | RO MENBRANE | GE/TORRAY/DOW/EUREKA FORBES
58 | ULTRAVIOLET UNIT | EUREKA FORBES/PENAIR
59 | Ozonisation System | Oraipl, Ozonics, Voltas
60 | SFRC Manhole Cover | KGM, KK, Nutek
61 | MH/Water Tank Plastic Steps | NECO, Patela, KGM
62 | Positive Displacement Diaphragm Pump | WALKTON/ GRUNDFOS/ LMI
63 | M.S. Steel (Angle. Channel, Strip, Sheet) | Tata, Sail, Jindal Hissar
64 | TDS METER | FORBESS MARSHAL/HONEYWELL/ASTER
65 | PH METER | FORBESS MARSHAL/HONEYWELL/WALKTON
66 | Paint | Berger, Asian
67 | Rain Water Harvesting | Bantair ,Ashwath Infratech Pvt. Ltd. Delhi., Life Green Systems,
68 | PVC Water Tank | SINTEX, SUPREME, VECTUS
69 | SS Pipe | J – Press, Geberit, Viega
70 | Self-Priming Pumps | Johnson, Kirloskar, KSB, Xylem
71 | AIR BLOWER | EVEREST/ BETA/ AKASH
72 | AIR DIFFUSER | REHAU/ OTT/ SCOGEN
73 | MS PIPES | TATA/ JINDAL/ SURYA
74 | ANOXIC MIXER | AQUA ITLY/3SW/ ATE
75 | UV SYSTEM | ALFA/ SUKRUIT
76 | SEWAGE HANDLING PUMP | GRUNDFOSS/KIRLOSKAR/ KSB
77 | SLUDGE RECIRCULATION PUMP | GRUNDFOSS/ LUBI/ KSB
78 | TUBE SETTLER MEDIA | MM AQUA/ COOLDECK
79 | ADVANCE MBBR MEDIA | KURRARAY/ HYDROCON
80 | FILTER PRESS | PHARMATECH/ AURO
81 | SCREW PUMP | ROTO/ KIRLOSKAR
82 | WATER SOFTNER | KANBE/3SW/ THERMAX
83 | MCC PANEL | MISTUBUSHI-RITAL
84 | CABLES | KEI/ POLYCAB/Finolex
85 | END TERMINATIONS | COMET/ DOWELL/ JAINSON
86 | CABLE TRAY | MEM/ RMCON/ STEELWAYS
LIST OF PREFERED MAKE FOR FIRE FIGHTING WORKS
Sl. | Materials | Approved Makes
No.
1 | M.S/G.I Pipe | TATA, Jindal( Hissar)
2 | Forged Steel Fittings | V.S Forge, DKR, Victaulic
3 | Sluice valves | Kirloskar, Zoloto,
4 | Butterfly Valves | Kirloskar, Zoloto,
5 | Non Return Valves | Kirloskar, Zoloto,
6 | Ball Valves | Kirloskar, Zoloto,
7 | Gate Valves | Kirloskar, Zoloto,
8 | Flow Switch | Potter, HD, System Sensor
9 | Pressure Gauge | Eversafe, H.Guru, Fiebig, Waree
10 | Hydrant valve | Safeguard, Exflame
11 | Fire Brigade Inlet | Safeguard, Exflame
12 | Hose pipe (C. P ) | Safeguard, Exflame
13 | Hose pipe (R.R.L.) | Safeguard, Exflame
14 | Hose Reel | Safeguard, Exflame
15 | Hose Coupling branch pipe and nozzle | Safeguard, Exflame
16 | Portable Fire Extinguisher | Safeguard, Exflame
17 | Gas Suppression System | SVS BUILDWELL, TYCO (ANSUL), MINIMAX, ROTAREX, FOAM TECH
18 | Electrical Panel Gas Suppression System | SVS BUILDWELL, FIRETRACE, MINIMAX, ROTAREX
20 | Flexible Hoses | VICTAULIC, TYCO, NEWAGE (GUJARAT)
21 | Sprinkler and accessories | HD, Tyco, Viking, Victaulic
22 | Deluge Valve | HD, Tyco, Viking, Victaulic
23 | Water Curtain Nozzle | HD, Tyco, Viking, Victaulic
24 | Wet Alarm Valve | HD, Tyco, Viking, Victaulic
25 | Pressure Reducing Valve | Honeywell, Danfoss, Newage
26 | Pipe coat material (Pipe Protection) | PYPKOTE,Rustfire, Corpro-Tape, Makpoly Cot
27 | Paint | Asian, Nerolac, Berger
28 | Fire Pumps | Kirloskar, KSB, Grundfos, Lubi
29 | Electrical Motors | Kirloskar, ABB, Crompton, Siemens
30 | Diesel Engine | Ashok Leyland, Kirloskar, Cummins, Lubi
31 | Vibration isolator/Flexible Coupling | Resisto flex, Kanwal Industries, Dunlop
32 | Strainer | Emerald, Kartar, Zoloto, Castle
33 | Anchor Fastener | HILTI, FISHER
34 | Supporting Material for piping | HILTI, FISHER
36 | Grooved Fittings | Victaulic, Viking, Tyco
37 | DI Fittings | Sant, Jainsons, New
38 | Fire Sealant | 3M, HILTI
39 | Intumescent Paint (2 hr Fire rating) | Nullifire, Jotun

## Light Fixture Schedule
ANNEXURE-2_ LIGHTING FIXTURE B.O.Q
S.No | DESCRIPTION OF LIGHT FIXTURE | SPECIFICATIONS | Make | Ref. Image | BLOCK-1 | BLOCK-2 | BLOCK-3 | DOG KENNEL | ARMORY | TOTAL QUANTITY | Rate | Amount
| 12W LED DOWNLIGHT (SURFACE MOUNTED) | 12W SURFACE MOUNTED LED LIGHT FIXTURE , DIA 170 MM & 35 MM HEIGHT , CODE – EDGE SURFACE ROUND PANEL 12) DOWNLIGHTER WITH 4000 K | HAVELLS/ PHILIPS |  | 950 | 1236 | 550 | 42 | 13 | 2791 | 950 | 2651450
| 9W WALL MOUNTED MIRROR LIGHT | 9W WALL MOUNTED LED LIGHT FIXTURE, L- 345mm x W-150mm x H- 85mm, 450lm | HAVELLS/ PHILIPS |  | 93 | 87 | 53 | 3 | - | 236 | 5200 | 1227200
| 20W WALL MOUNTED LIGHT | Bulb Type- E27 (Bulb Not Included) , Dimension 100mm (length)x125mm (width)x200mm(height) | HAVELLS/ PHILIPS |  | 5 | - | - | 24 | 4 | 33 | 3550 | 117150
| 12W LINEAR LED LIGHT (WALL MOUNTED) | 12W LED Linear Extruded Aluminium Surface Luminaire , System Efficacy 110 Lumens per Watt, THD<10%,PF>0.95, CCT 4000K/5700K, IP20 | HAVELLS/ PHILIPS |  | - | - | - | 14 | - | 14 | 3500 | 49000
| 12W LED DOWNLIGHT (RECESSED) | 12W LED RECESS DOWNLIGHTER , ALUMINIUM HOUSING,SYSTEM EFFICACY 100 LUMENS PER WATT, THD<10%,PF>0.95, CCT 4000K/5700K, IP20 | HAVELLS/ PHILIPS |  | 56 | - | 10 | 34 | - | 100 | 750 | 75000
| 20W LINEAR LED LIGHT (CEILING SUSPENDED MOUNTED) | Supply of LED based suspended standalone 4ft. Luminaire with a nominal system lumen output of 2500 lumens with Downward light ratio and a minimum system efficacy of 120 lm/W. The LED driver shall be accessible without opening the LED compartment. The driver acess shall be from the backside of the luminiare.The luminaire shall have a color temperature of 6500K and CRI≥80. The luminaire shall be made up of extruded aluminium and meet IP20 Rating with THD≤10% and PF≥0.9. The total Power Consumption should not exceed 20 W (including Driver). Dimensions :- 1120mm x 53mm x 70mmThe luminare driver shall be of the same make/manufacturer/brand as that of LED luminaires. The luminaire & driver shall have BIS registration & the bidder shall submit the BIS certificates along with technical BID. The LED luminaire manufacturer should have in-house NABL accredited lab to conduct type test, factory acceptance test before dispatch of material, LM79 test & IK test. The bidder shall submit the NABL accreditation of LED luminaire manufacturer along with technical bid. The bidder shall submit the Type test of luminaires & LM79 test reports issued by NABL accredited lab before supply of material. Product complying to above specs in Signify, LT or Endo. | HAVELLS/ PHILIPS |  | 161 | - | - | - | - | 161 | 3500 | 563500
| 25W DOWNLIGHT (RECESSED) | PHILIPS/ Supplying of recessed type LED 2x2 luminaire with CRCA housing suitable with fully diffused PS diffuser for general lighting in office areas. The luminaire should have a color consistency SDCM < 5, CRI 80 and CCT of 4000K. The luminaire shall be compliant with IP20 and IK02 classification. Luminaire shall be designed to emit at least 3000 nominal lumens and an outstanding backlit solution efficacy of atleast 120 lumen/watt and maximum system wattage of 25W. The luminaire shall be designed so as to ensure L70B50 @ 50K Hrs.@ 45 Degree Ambient. The electronic driver used shall have a power factor >0.95 and THD <10% The fixture should comply with the parameters as per IS10322. Similar to RC380B LED30S-6500 G5 L60W60 PSU OD | HAVELLS/ PHILIPS |  | 6 | - | - | - | - | 6 | 2000 | 12000
| 38W LED STRIP LIGHT | Supply of LED strip light, white and uncoated synthetic, 38W/5mtr, 240V, 50Hz, IP20 with nominal system lumens 4000lm/5 mtr, Life of strip with driver : 30000 burning Hrs.@L70B50 Lumen maintenance, CCT of 4000K, CRI>80, SDCM<=3 with driver. Similar to LS170S LED8 S 840 IP20 L5000 PRO. Make-Signify | HAVELLS/ PHILIPS |  | 10 |  |  |  |  | 10 | 5000 | 50000
|  | TOTAL COST ( EXCLUDING TAXES AS APPLICABLE) | [9 empty] | 4745300
NOTE – VENDOR HAS TO GET APPROVAL FOR ALL THE SAMPLES FROM INCUBIS & CLIENT PRIOR TO MASS ORDERING & INSTALLATION AT SITE.

## Electrical Makes
LIST OF APPROVED MAKES FOR ELECTRICAL WORKS
Instruction to bidders:
1) Submit catalogues with the offers.
2) Produce test certificates for equipment/ material supplied with bills for certification.
3) Submittals and samples must be gotten approved before supply, from Owner/ Project Managers/ Architect/ Consultants.
4) In case any of makes for any of the material is missed out in the above list for using at site then the contractor shall inform the Engineer-in-charge/ Consultants about the same and obtain the approval. Thereafter, he can proceed with the supply of the material
S.No. | Description | Makes
1 | Battery Charger | Crompton Greaves/ Delta
2
3 | MS conduit (ISI Marked) | BEC/ Precision/ RMCON
4 | Modular Plate, Modular Switch/ Sockets, TV Socket outlet, GI Boxes, Fan Regulator, Industrial Socket Outlet (ISI marked) | Legrand/ MK
5 | 1.1kV Grade PVC insulated FRLS single core cable/ wire (ISI Marked) | KEI/ Polycab/finolex
6 | PVC conduit with accessories (ISI marked) | BEC/ Precision/ AKG
7 | TV cable/ Telephone cable | KEI/ Havells ,finolex
8 | Telephone Tag Blocks | Krone Type (German)/ D-Link/ R&M
9 | Moulded Case Circuit Breaker (MCCB) | Siemens , Legrand , Schneider
10 | MCB/ Distribution Boards/ Isolator/ ELCB/ RCCB | Legrand/ Schneider
11 | Lighting Conductor/ Protection & Earthing System | APS/ Dehn/ OBO/ JMV/CAPE
12 | Cable Tray (Factory Fabricated) | MEM/ BEC,Legrand
13 | Floor Raceway System | MEM/ BEC,Legrand
14 | UPS system | Emerson/ Delta/ TMEIC
15 | LED Light Fixture | Havells/ PHLIPS
16 | Ceiling Fan/ Wall Fans/ Exhaust Fans/ Pedestal Fans | Crompton/ Havells
17 | External Lighting/ Lighting Fixtures | Wipro/ Havells
K-Lite
18 | External lighting Pole | Wipro/ Havells
K-Lite
19 | Occupancy Sensor | Phillips/ Wipro/ Honeywell/ Finder/ Lutron
20 | Ploycarbonate Junction Box | MK/ Legrand
21 | Insulation Mats/ Rubber Mats | Jyoti/ Maruti/ Agni/ Howeil/ Fire hut
22 | Bus Duct/ Rising Main/ Tap off Box | Legrand/ Schneider/ L&T/ C&S/ EAE/ RR Global
23 | MV Panel/ LT Panel/ Feeder Pillar | C&S,Siemens ,Schneider
24 | Rubber Gaskets | CIC/ Varuna/ Jyoti/ Agni
25 | Selector Switch’s | L&T/ Kaycee/ AE/ Salzer/ Siemens
26 | ACB’s | ABB,Siemens ,Schneider
27 | LED Indication Lamps/ Push button | Schneider Electric/ Vaishno Electricals/ Siemens/ L&T/ Conserve/ C&S
28 | APFC/ Capacitor Panel | Schneider/ ABB/ L&T/ Siemens/
Epcos
29 | Capacitors | Epcos/ L&T/ BCH/ Neptune
30 | CT’s/ PT’s | Automatic Electric/ Pragati/ Kappa/ L&T/ Neptune
31 | Electronic Digital Meters (A/V/PF/Hz/KW/KWH) with LED Display | Neptune/ L&T/ Schneider-Conserv/ Secure/ Socomec
32 | Automatic Transfer Switch | ASCO/ Socomec
33 | SPD (Surge Protector) | Dehn/ Eaton/ LPI/ ERICO/ CAPE/ OBO/
34 | Earth Leakage Protection relay/ Aux. Relay/ APFC Relay/ PLC | L&T/ Schneider/ Legrand/ C&S/ Neptune/ Siemens
35 | Digital Astro Timer | Legrand/ L&T/ C&S/ ABB/ Havells/ Finder
36 | Power Contactor/ Aux. Contactor (Model to be compelled with System) | L&T/ Siemens/ Legrand/ Schneider/ C&S
37 | Single Phase Preventer | Minilec/ Siemens/ Legrand/ L&T
38 | XLPE Aluminium/ copper Conductor Armoured LT cables upto 1100 V Grade (ISI Marked) | KEI/ POLYCAB/Finolex
39
40 | End Termination/ Brass compression gland | Dowell's/ Comet/ Raychem/ Gripwell/ Jainson/ ABB
41 | DWC HDPE Pipe (ISI Marked) | Rex/ Duraline/ Tirupati/ GF/ BEC
42 | Jointing Kit/ Cable Gland/ Lugs/ Thimbles/ Compression Glands | Comet/ Dowells/ Raychem/ Gripwell/ ABB/ Jainson/ Denson
(HT/ LT)
43 | Starters | L&T/ Siemens/ Schneider
44 | Fire Extinguisher | Lifeguard/ Ceasefire/ Minimax/ Safex
45 | Fire Extinguishing System/ Suppression System | Lifeguard/ Minimax/ Safex/ Cease fire
46 | Synthetic Enamel Paints/ Primer | Asian/ Berger/ Nerolac/ ICI
47 | Addressable Fire Alarm/ Smoke Detection system and all its components (UL Listed) | Notifier/ Bosch/ Edwards/ Siemens/ Johnson controls
48 | Fire Survival Armored Cable | RRKabel/ KEI/ Havells/ Batra Henlay/ Bonton/ Gloster/ Ravin
49 | Heat Detector/ Response Indicator/ Manual Call Point/ Fault Isolator/ Monitor Module/ Hooter/ Probe/ Monitor Module/ Beam Detector/ Speaker/ Fire Fighter Jack and all other components | Notifier/ Bosch/ Edwards/ Siemens/ Johnson controls
50 | Operator’s workstation (Computer) | Sumsung/ HP/ IBM/ Lenovo
51 | Laser jet printer | Epson/ HP/ Canon
52 | Software (For fire alarm) | Notifier/ Edwards/ Bosch/ Siemens/ Johnson controls
53 | Desktop PC | HP/ Panasonic/ Dell/ Lenovo
54 | Copper/ Aluminium conductor control cable | RRKabel/ KEI/ Havells/ Batra Henlay/ Bonton/ Gloster/ Ravin
55 | Communication cable / signal cable | RRKabel/ KEI/ Havells/ Batra Henlay/ Bonton/ Gloster/ Ravin
56 | Digital Voice Equacuation System | Notifier/ Bosch/ Honeywell/ Edwards/
Siemens/ Johnson Control/ Henrich
57 | Speaker/ Array Speaker/ Sub-woofer | Bosch/ Martin Audio/ Henrich/ Aties
58 | PA System | Bosch/ Martin Audio/ Henrich/ Ateis
59 | Amplifier/ Processor | Bosch/ Martin Audio/ Henrich/ Ateis
60 | IP Based Phone | Avaya/ Cisco/ HP/ Mytel
61 | Fire Sealent | Birla 3M/ Hilti/ VGA
LIST OF APPROVED MAKES FOR ELV SERVICES WORKS
S.No. | Description | Makes
1 | IR IP bullet camera | Bosch , Honeywell
2 | IP Dome camera | Bosch , Honeywell
3 | IR PTZ Camera | Bosch , Honeywell
4 | Video management solution complete with server, hardware, VMS & storage/ NVR/ ANPR System | Bosch , Honeywell
5 | Access Control System | Honeywell/ Dorma Kaba/ Suprems/ Morpho/ IDCUBE/ Gallagher
6 | Workstation | Dell/ HP/ Lenovo/IBM.
7 | LED Monitor/ LED Display | Samsung / Panasonic/ Sony
8 | Network Switches | Cisco / Extreme / Juniper
9 | Patch cord | Siemon / Schneider / Legrand
10 | Fiber Panels (LIU) fully loaded with Pigtails | Siemon / Schneider / Legrand
11 | Patch Panel | Siemon / Schneider / Legrand
12 | Single Mode/ Multi Mode fiber Optical cable | Siemon / Schneider / Legrand
13 | CAT 6A U/ FTP Cable | Siemon / Schneider / Legrand
14 | Network Rack | MTS/ Legrand
15 | Speakers of all type | Electro Voice (By Bosch)/ JBL (By Harman)/ Bose/ QSC/ Martin Audio/ Toa/ Crestron/ Kramer
16 | Amplifiers | Electro Voice (By Bosch)
17 | Digital Signal Processor | Electro Voice (By Bosch)
18 | Microphone (Wired/ Wireless) | Electro Voice (By Bosch)
19 | Projector/ Projector Lens | Panasonic/ Sony
20 | Projector Brackets | As per OEM
21 | Projection screen | Draper/ Dalite/ Suvira/ Starway/ Liberty
22 | Display panels | Samsung/ Delta/ Planer/ Panasonic/ LG/ Sony
23 | Cables and Connectors | MX
24 | HDMI Switcher/ Audio deembedder | Kramer/ Extron/ Light Ware/ BiAmp/ Crestron/ AMX/ Liberty
25 | Digital Podium | Bronx/ Dalite/ E-Learn/ MTS / Vantage/ AHA / Ordain
26 | PTZ Camera/ Auto Tracking Camera/ Joystick | Bronx/ Lumens/ Panasonic/ Vaddio/ Sony/ Avaya
27 | Audio Video Conference | Zoom/ Microsoft Team/ Webex
(Software/ Hardware Based)
28 | HDMI Cable/ Patchcords | Krystal/ Kramer/ Extron/ Falcon/ Klotz/ Crestron/ Sennheiser/ Bosch/ Televic/ Taxker/ Aten
29 | Microphone/ Speaker cable | Krystal/ Kramer/ Extron/ Falcon/ Klotz/ Crestron/ Sennheiser/ Bosch/ Televic/ Taxker
30 | Cat 6 Cable | Belden/ Panduit/ Molex/ R&M/ Derwiser/ Siemon/ Schneider/ Legrand
31 | USB extender | Extron/ Kramer/ Crestron
32 | Conference Unit/ Delegate Discussion Unit/ Chairman Discussion Unit | Bronx/ Brahler/ Bosch/ Sennheiser/ Beyerdynamics/ Shure/ Televic
33 | Patchcords/ cables | Belden/ Panduit/ Molex/ R&M/ Derwiser/ Siemon/ Schneider/ Legrand
34 | Gigabyte Router/ Network Switch/ Patch panel | Cisco/ Juniper/ Extreme/ Arista
35 | Tablet/ PC/ Workstation/ Server | Samsung/ HP/ Dell/ Lenovo
36 | Interactive display on Podium | Wacom/ Elmo/ QSC/ Kramer/ Samsung/ HP
37 | Document Camera | Wolfvision/ Lumens/ Elmo/ Avaya
38 | Rack | MTS/ Legrand
39 | Firewall system | Cisco
40 | Indoor/ outdoor access point | Cisco
41 | IP Phone | Cisco
42 | IP-PBX system/ IP Phone | Cisco
43 | Wi-Fi System | Cisco
LIST OF PREFERED MAKES FOR BMS WORKS
S. NO. | EQUIPMENT / MATERIAL | MANUFACTURER/ SUPPLIER/ MAKE
1 | Central Control BMS Server | HP / DELL / Lenovo
2 | Monitor | HP / DELL / LG / Samsung
3 | Printer | HP / Canon / Epson
4 | Building Management Web Based Server Software | Desigo by Siemens / ALC by Carrier / Metasys by Johnson / EBI by Honeywell
5 | Direct Digital Controller (DDC) | Desigo by Siemens/ ALC by Carrier / Easy-IO by Johnson / Honeywell Comfort Point
6 | Integartor | Desigo by Siemens/ ALC by Carrier / Easy-IO by Johnson / Honeywell Comfort Point
7 | Network Switches | Cisco / Extreme Networks/ Hp , Juniper
8 | Enclosure for Controllers | Rittal / BCH Electric Limited / Fibox
9 | Outside Temp+RH Sensor | Siemens / Honeywell / Carrier ALC / Johnson Control
10 | Immersion type temperature sensors | Siemens / Honeywell / Carrier ALC / Johnson Control
11 | Differential pressure Switch / Sensor (Air & Water) | Siemens / Honeywell / Carrier ALC / Johnson Control
12 | Duct type Static Pressure Sensor | Siemens / Honeywell / Carrier ALC / Johnson Control
13 | Room / Duct Temp Sensor | Siemens / Honeywell / Carrier ALC / Johnson Control
14 | Temp+RH Sensor | Siemens / Honeywell / Carrier ALC / Johnson Control
15 | Pressure Sensor Water | Siemens / Honeywell / Carrier ALC / Johnson Control
16 | Water Level Switches | Veksler / Flipro / Dwyer / Omicron
17 | Flame Proof Level Transmitter | Veksler / Flipro / Dwyer / Omicron
18 | DC Voltage /Current/Power Factor Transducer | ABB / Rishab / Dwyer / Omicron
19 | Current Relay | L&T / ABB / Dwyer / Omicron
20 | PH Anayser/ TDS Analyser | Hach / ABB / Omicron
21 | Ultrasonic BTU Meter/Flow Meter | Siemens / Honeywell / Carrier ALC / Johnson Control
22 | IAQ Multi Sensor | Siemens/ Kaiterra/ Milesight/ Belimo
23 | CO2 Sensor | Siemens / Honeywell / Carrier ALC / Johnson Control
24 | Signal Cable / Communication Cables | KEI / Bonton / Polycab / Rallison
25 | CAT6 | Digilink/ Sterlite/ Commscope/ Molex
26 | Optical Fibre Cables | Beldon/ Siemon/ Commscope/ Panduit
27 | PVC Conduit | BEC / AKG / RMCON
28 | MS/GI / Flexible Conduit | BEC / AKG / RMCON
29 | Cable Trays | MEM / Pilco / STEELWAYS / Profab / Slotco / Rmcon