Tender No:. 2025-26/Estate/2B/LNM-1162

The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “Rehabilitation, repair, and re-waterproofing of terrace water tanks of the G+6 hostel building”. Bidders can submit their sealed offers/s at the following address by Email/Speed-Post/ Registered Post/ By-hand/courier before 05:00 PM on 31/10/2025 (Last date of bid submission).

Filing of Tender:

Option 1: Physical submission of offers (hard copy) in sealed envelopes.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the institute in person/ Speed-Post/ Registered Post/ By-hand/courier of the Institute after marking due entries in the Receipt Book available with the Security Officer at the main gate.

The tender subject and reference number must be mentioned on the envelope.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Option 2: Password-protected online submission via Email

Password-protected offers can be submitted by the bidders via email at the below-mentioned email IDs.

tender-document@lnmiit.ac.in (password-protected document)

tender-password@lnmiit.ac.in (password only)

The tender subject and reference number must be mentioned in the subject line of the emails.

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory, are required to be submitted in two separate envelopes/emails.

Envelopes/Emails should be duly marked as follows:

- Technical bid for “Rehabilitation, repair, and re-waterproofing of terrace water tanks of the G+6 hostel building”.

- Commercial Bid for the “_Rehabilitation, repair, and re-waterproofing of terrace water tanks of the G+6 hostel building”.

- Both Envelopes/files should be enclosed/attached in a single envelope/email bearing the heading for “_Rehabilitation, repair, and re-waterproofing of terrace water tanks of the G+6 hostel building”..(Tender No. : 2025-26/Estate/2B/LNM-1162) ”.

Bids are liable to be rejected:

- If the above-mentioned bid submission procedure is not followed.

- Incomplete and non-conforming bids.

- Arbitration: All disputes and differences arising between the two parties in connection with this order shall be mutually settled as far as possible, failing which, all such disputes shall be referred to arbitration and settlement under the provision of the Arbitration and Conciliation Act, 1996 and as amended from time to time or any such law for the time being prevailing in India. The venue of such arbitration shall be Jaipur.

Technical Bid: (in a separate sealed envelope/via email)

# Bid for Rehabilitation, repair, and re-waterproofing of terrace water tanks of the G+6 hostel building

# (Tender No. : 2025-26/Estate/2B/LNM-1162)

Bidder is required to furnish the requisite details as per the below mentioned table format and proof of such documents to be uploaded along with the bid under respective title/ headings as mentioned at column no ‘C’ accordingly.

| ## SL NO. | ## Title/ Heading ## Details sought by buyer | ## Details/ Certificate No. (Attached Y/N) |
| --- | --- | --- |
| ## A | ## B | ## C |
| ## 1. | ## Bidder Firm Name & Registration No, |  |
| ## 2. | ## Bidder’s Company profile or brief note |  |
| ## 3. | ## PAN Card No,. |  |
| ## 4. | ## GST Number |  |
| ## 5. | ## List of Directors/ Partners/Proprietor/ Members of the Bidder’s Firm |  |
| ## 6. | ## Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members |  |
| ## 7. | ## Bidder Turnover - Average annual turnover for last three years |  |
| ## 8. | ## The Client List with some purchase orders and satisfactory certificate (to whom the vendor has delivered the goods/provided the services in the past (Three (03) purchase orders/work orders, at least one from each of the last three years, including the previous year.) |  |
| ## 9. | ## If the bidder is authorized by the OEM/Manufacturer. Proof of the same is to be submitted with the Technical Bid |  |

Scope of Work:
The work involves rehabilitation, repair, and re-waterproofing of terrace water tanks of the G+6 hostel building for 240 students, including potable water tanks, flushing water tanks, and the fire water tank. The contractor shall carry out all necessary preparatory, repair, waterproofing, testing, and handover activities as per the approved methodology.

The tanks include:

- Potable water tanks

- Flushing water tanks

- Fire-fighting water tank

The tanks have reported dampness, leaks, and minor structural defects, requiring a combination of structural repair, PU waterproofing, GP2 external plastering, and testing to restore full serviceability and watertightness.

Contractor Responsibilities

The contractor shall be responsible for:

- Providing all labour, tools, scaffolding, safety equipment, and materials.

- Carrying out preparatory, repair, rehabilitation, waterproofing, testing, and handover activities as per approved methodology.

- Ensuring potable water safety by using only approved potable-grade materials inside potable tanks.

- Maintaining safety and access to the terrace and tanks during all works.

- Coordinating with the Engineer-in-Charge for inspections, approvals, and testing.

Detailed Work Components

Preliminary Works

- Mobilization of labor, materials, and equipment.

- Preparation of access and scaffolding to safely reach all tanks.

- Draining of tanks, isolation from water supply, and temporary water management (Arrange temporary HDPE tanks to maintain hostel water supply).

- Site inspection and documentation of existing conditions (cracks, dampness, leakage, concrete defects).

Dewatering, Cleaning, and Surface Preparation

- Complete dewatering of all tanks using pumps.

- Removal of silt, debris, and loose particles.

- High-pressure water jet cleaning of internal surfaces (walls, floors, corners).

- Mechanical chipping of delaminated, honeycombed, or weak concrete.

- Cutting fillets and edges where required to prepare surfaces for rehabilitation.

Structural Repair and Rehabilitation

- Crack Treatment:

  - Inject epoxy or PU grout into cracks >0.3 mm width.

  - Ensure complete penetration and sealing of all active cracks.

- Honeycombs / Spalled Areas:

  - Apply polymer-modified mortar or cementitious repair mortar.

  - Restore profile to original dimensions.

- Reinforcement Repair:

  - Expose and treat corroded steel.

  - Replace or supplement reinforcement if required.

- Fillets:

  - Form 50×50 mm fillets at wall-floor and wall-wall junctions using polymer mortar.

Primer / Bond Coat

- Apply potable-grade PU primer to all prepared internal surfaces.

- Ensure complete and uniform coverage to achieve proper adhesion of waterproofing membrane.

PU Waterproofing Membrane Application

- Apply potable-grade PU waterproofing in two coats:

- First coat: ~0.6 mm thickness

- Second coat: perpendicular to first, total DFT ~1.2 mm

- Extend coating to corners, joints, and fillets for seamless coverage.

- Ensure proper curing for 48–72 hours before water contact.

Floor Protective Screed

- Apply polymer-modified cement mortar screed (~20 mm thick) over the cured PU membrane on floors.

- Maintain slope toward outlets for drainage.

- Cure screed for 3 days with wet hessian or misting.

External Bottom Plastering (GP2)

- Clean and roughen external bottom slab.

- Apply GP2 cementitious plaster (25 mm thick) for levelling and seepage prevention.

- Over GP2, apply polymer-modified render (~10 mm) for protection.

- Cure plaster for 3 days.

Pipe Penetrations and Joint Sealing

- Expose all inlet, outlet, overflow, and fire connections.

- Seal pipe collars and penetrations using PU sealant or polymer mortar.

- Install mechanical sleeves or puddle flanges where necessary.

- Ensure watertight integration with internal PU membrane and external GP2 coat.

Hydrostatic (Flood) Testing

- Conduct flood test on all tanks after curing for 72 hours.

- Inspect all surfaces and joints for leakage or dampness.

- Repair any defects and retest until watertight.

- Record testing observations for submission.

Disinfection and Handover

- Clean tanks internally with clean water.

- Disinfect potable tanks with chlorine solution (~50 ppm).

- Flush thoroughly to ensure safe potable water supply.

- Submit completion report including test results, photographs, and material approvals.

Materials and Standards

- PU Waterproofing: Potable-grade, seamless, UV-resistant, flexible, 1.2 mm DFT (Fosroc, Sika, Dr. Fixit, BASF)

- GP2 Plastering: Non-shrink cementitious plaster (Sika Grout 214, Renderoc GP2)

- Polymer Mortars: SBR-modified, for repairs and fillets

- Sealants: PU-based sealants for joints and penetrations

- Concrete Repair: Polymer-modified or epoxy mortars for structural rehabilitation

- All materials to comply with relevant IS/BS/ASTM standards for potable water and structural performance.

Quality Assurance & Documentation

- Material data sheets and manufacturer approvals

- Stepwise work completion records

- Hydrostatic testing reports

- Photographic documentation of repairs, waterproofing, and plastering

- Completion certificate and 5-year waterproofing performance guarantee

Technical specification:

| Sr. No. | Item Name | Qty. | UOM |
| --- | --- | --- | --- |
| 1 | Rehabilitation, repair, and re-waterproofing of terrace water tanks of the G+6 hostel building for 240 students, including potable water tanks, flushing water tanks, and the fire water tank. The contractor shall carry out all necessary preparatory, repair both internal and external, waterproofing, testing, and handover activities as per the approved methodology. | 193.036 | Sqm |

Note: - “The actual scope of work is indicative and may change as per site conditions and the instructions of the Engineer-in-Charge. Final approval shall be obtained at site before execution.”

Signature with seal

Commercial Bid: (in separate sealed envelope/password protected file via email)

# Bid for Rehabilitation, repair, and re-waterproofing of terrace water tanks of the G+6 hostel building

(Tender No. : 2025-26/Estate/2B/LNM-1162)

| S.No. | Item Name/ Description | Qty. | UOM | Rate | Amount |
| --- | --- | --- | --- | --- | --- |
| 1. | Rehabilitation, repair, and re-waterproofing of terrace water tanks of the G+6 hostel building for 240 students, including potable water tanks, flushing water tanks, and the fire water tank. The contractor shall carry out all necessary preparatory, repair both internal and external, waterproofing, testing, and handover activities as per the approved methodology. | 193.036 | Sqm |  |  |
| Total |  |  |  |  |  |
| GST |  |  |  |  |  |
| Total including GST |  |  |  |  |  |

Note: - “The actual scope of work is indicative and may change as per site conditions and the instructions of the Engineer-in-Charge. Final approval shall be obtained at site before execution.”

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should	include everything (packing, forwarding, transit insurance, transportation, loading /unloading, installation etc.). Loading/unloading up to 50 mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- The bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only.

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

- All charges applicable shall be clearly mentioned in the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

Signature with seal