# Tender No:. 2025-26/ESTATE/2B/LNM-1233

The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “SITC of chemical Earthing’s”. Bidders can submit their sealed offers/s at the following address by Email/Speed-Post/ Registered Post/ By-hand/courier before 05:00 PM on 09.01.2026 (Last date of bid submission).

Filing of Tender:

Option 1: Physical submission of offers (hard copy) in sealed envelopes.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the institute in person/ Speed-Post/ Registered Post/ By-hand/courier of the Institute after marking due entries in the Receipt Book available with the Security Officer at the main gate.

The tender subject and reference number must be mentioned on the envelope.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Option 2: Password-protected online submission via Email

Password-protected offers can be submitted by the bidders via email at the below-mentioned email IDs.

tender-document@lnmiit.ac.in (password-protected document)

tender-password@lnmiit.ac.in (password only)

The tender subject and reference number must be mentioned in the subject line of the emails.

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory, are required to be submitted in two separate envelopes/emails.

Envelopes/Emails should be duly marked as follows:

- Technical bid for the: SITC of chemical Earthing’s (The technical bid must be submitted without password protection)

- Commercial Bid for the:  SITC of chemical Earthing’s (The commercial bid must be submitted with password protection.)

- Both Envelopes/files should be enclosed/attached in a single envelope/email bearing the heading “Bid for SITC of chemical Earthing’s (Tender No. : 2025-26/Estate/2B/LNM-1233)”.

Bids are liable to be rejected:

- If the above-mentioned bid submission procedure is not followed.

- Incomplete and non-conforming bids.

- Arbitration: All disputes and differences arising between the two parties in connection with this order shall be mutually settled as far as possible, failing which, all such disputes shall be referred to arbitration and settlement under the provision of the Arbitration and Conciliation Act, 1996 and as amended from time to time or any such law for the time being prevailing in India. The venue of such arbitration shall be Jaipur.

Technical Bid: (in a separate sealed envelope/via email)

# Bid for “SITC of chemical Earthing’s”

# (Tender No. : 2025-26/Estate/2B/LNM-1233)

Bidder is required to furnish the requisite details as per the below mentioned table format and proof of such documents to be uploaded along with the bid under respective title/ headings as mentioned at column no ‘C’ accordingly.

| S.No. | Title/ Heading Details sought by buyer | Details/ Certificate No. (Attached Y/N) |
| --- | --- | --- |
| A | B | C |
| 1. | Bidder Firm Name & Registration No, |  |
| 2. | Bidder’s Company profile or brief note |  |
| 3. | PAN Card No,. |  |
| 4. | GST Number |  |
| 5. | List of Directors/ Partners/Proprietor/ Members of the Bidder’s Firm |  |
| 6. | Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members |  |
| 7. | Bidder Turnover - Average annual turnover for last three years |  |
| 8. | The Client List with some purchase orders and satisfactory certificate (to whom the vendor has delivered the goods/provided the services in the past (Three (03) purchase orders/work orders, at least one from each of the last three years, including the previous year.) |  |
| 9. | If the bidder is authorized by the OEM/Manufacturer. Proof of the same is to be submitted with the Technical Bid |  |
| 10. | An undertaking (self-certificate) that the agency has not been blacklisted by a Central/State/UT Government Institutions and there has been no litigation with any government department/institution on account of any services/supplies. |  |
| 11. | Scanned copy of EMD/ Tender Fees paid through RTGS/NEFT (if required/asked in the tender) |  |
| 12 | Xerox copies of MoUs with previous colleges (minimum three) must be attached. (Applicable for student fest only). |  |

- Technical specification:

Scope of Work

Supply, Installation, Testing & Commissioning of Chemical Earthing System

The scope of work shall include design, supply, installation, testing and commissioning of complete Chemical Earthing System (GI) as per CPWD specifications, relevant IS codes, and directions of the Engineer-in-Charge.

1. Chemical Earthing Electrode (GI)

- Supply and installation of GI Chemical Earthing Electrode,

  - Length: 3.0 meters

  - Diameter: 50 mm

- Electrode shall be installed vertically in the ground at approved locations.

- Backfilling shall be done using Ground Enhancing Compound (GEC) around the electrode as per manufacturer’s recommendations.

- Earthing electrode shall be provided with necessary watering arrangement, GI funnel, wire mesh, and protective accessories.

- All materials shall conform to IS: 3043

- GI material shall conform to IS: 1239 / IS: 3589 as applicable.

2. Earthing Pit Chamber Construction

- Construction of earthing pit chamber of internal size 450 mm × 450 mm (or as approved).

- Brick masonry using first-class bricks in cement mortar (1:4).

- Internal and external plastering with 12 mm thick cement plaster (1:4) finished smooth.

- Providing and fixing heavy-duty earthing pit cover (GI/CI) with:

  - Hinged or removable type

  - Locking arrangement

  - Load-bearing suitable for pedestrian area

- Chamber top level to be finished flush with surrounding ground / floor level.

3. GI Earthing Strip

- Supply and installation of GI strip 25 mm × 6 mm from earthing pit to equipment / earthing bus / route as shown in drawings.

- GI strip shall be laid:

  - In trenches, walls, or surface as per site conditions

  - Fixed using GI saddles, clamps, nuts, bolts and washers

- All joints shall be properly cleaned, overlapped, bolted and protected against corrosion.

- Route shall be approved by Engineer-in-Charge prior to execution.

- Strip shall be hot dip galvanized and conform to IS: 1730 / IS: 2629.

4. Earth Resistance Testing

- Measurement of earth resistance value using calibrated earth megger after completion of installation.

- Testing shall be carried out in the presence of the Engineer-in-Charge.

- Earth resistance value shall be maintained as per IS: 3043 standards (generally ≤ 1 Ohm or as specified).

- Submission of test reports for each earthing pit.

- Quantity: Job (Complete Work)

5. Painting & Identification

- Applying two coats of approved enamel paint (green / yellow) on:

  - Exposed GI strip

  - Earthing chamber identification markings

- Marking of earthing pit number and equipment name using durable paint.

6. General Requirements

- All works shall be carried out strictly as per:

  - IS: 3043 (Code of Practice for Earthing)

  - Safety rules and site instructions

- Contractor shall arrange all tools, tackles, testing instruments, labour, scaffolding, excavation, backfilling, and disposal of debris.

- Any damage to existing structures/services during execution shall be repaired at contractor’s cost.

- Work includes excavation in all kinds of soil, refilling, compaction, and making good the area.

7. Process for Connecting of Earthing Strips (GI 25 × 6 mm)

Connection Between Earthing Electrode and GI Strip

- The GI earthing strip (25 × 6 mm) shall be connected to the earthing electrode using:

  - GI bolts, nuts, spring washers and flat washers (minimum M10 size)

  - OR approved GI clamp suitable for chemical earthing electrode

- Contact surfaces shall be:

  - Cleaned by wire brushing / emery paper to remove rust, paint, oil, or oxide layer

  - Treated with anti-corrosive conductive compound before tightening

- Joint shall be mechanically strong and electrically continuous.

Strip Jointing Method (If required)

- Where GI strip length is not continuous, joints shall be made by:

  - Minimum 100 mm overlap

  - Secured with minimum two GI bolts, nuts & spring washers

- Welding shall not be permitted unless specifically approved by Engineer-in-Charge.

- After jointing, the joint shall be:

  - Cleaned

  - Coated with bituminous paint / anti-corrosive paint

  - Wrapped with protective tape where buried underground

Routing & Fixing of Earthing Strip

- Earthing strip shall be routed:

  - Along walls / ceilings / trenches as per approved drawings

  - Avoiding sharp bends (minimum bending radius ≥ 8 times strip width)

- Fixing shall be done using:

  - GI saddles / clamps at spacing:

    - 600 mm for horizontal runs

    - 1000 mm for vertical runs

- Strip shall not be embedded directly in concrete unless sleeved.

Connection to Equipment / Earthing Bus

- GI strip shall be terminated on equipment / panel / earthing bus bar using:

  - Properly sized GI lugs

  - GI bolts, nuts and washers

- A test link (disconnecting link) shall be provided near equipment / pit for testing and maintenance.

- Earthing continuity shall be ensured from electrode to final termination point.

Underground Installation

- Where earthing strip is buried underground:

  - Minimum depth: 600 mm

  - Laid on sand bed and covered with soft soil

  - Protected by PVC sleeve / brick protection at crossings and vulnerable locations

- Route shall be clearly marked on as-built drawings.

Corrosion Protection

- All exposed GI strips and joints shall be:

  - Cleaned

  - Painted with two coats of approved anti-corrosive enamel paint

- Buried joints shall be coated with bituminous paint before backfilling.

8. Compliance & Acceptance

- All earthing connections shall comply with:

  - IS: 3043

  - CPWD Electrical Specifications

- Final acceptance shall be subject to:

  - Visual inspection

  - Continuity testing

  - Earth resistance values within permissible limits

| S.No. | ITEM DESCRIPTION | UOM | QTY |
| --- | --- | --- | --- |
| 1 | Supply, Installation, Testing & Commissioning of Chemical Earthing System (GI) - 3meter Length 50 mm Dia, With GEC. (Ground Enhancing Compound) | Nos | 9 |
| 2 | Construction of pit chamber: Brick masonry (450 mm) with cement plaster 12 mm thick with heavy duty earthing pit cover (GI / CI) with locking arrangement (size as per pit) | Nos | 9 |
| 3 | Supply & installation of GI strip 25 × 6 mm (from pit upto equipment / upto route) including saddles/clamps | Mtr | 150 |
| 4 | Earth Testing | Job | 206 |
| 5 | Paint work on earth chamber | Nos | 9 |

Annexure

To Whomsoever It May Concern

This is to confirm that we, the undersigned, intend to participate in Tender No. : 2025-26/Estate/2B/LNM-1233 (Tender Number) for the tender/work titled: “SITC of chemical Earthing’s” (Item Name)”

We hereby certify the following:

No Conflict of Interest:

- We declare that we have no conflict of interest in participating in the above tender. We further confirm that we are not engaged in any activity or association that may compromise, or be perceived to compromise, our impartiality or ability to fulfil the obligations of the tender.

Undertaking on Blacklisting & Litigation (Self-Certificate):

- We hereby undertake that:

- Our agency/firm has never been blacklisted or debarred by any Central Government, State Government, Union Territory administration, or any other Institution/Organization.

- There is no ongoing or past litigation against our agency/firm with any Central Government, State Government, Union Territory administration, or any other Institution/Organization on account of any services/supplies.

- If at any stage the above declaration is found to be false, the Institute shall have the right to take any action as deemed appropriate, including rejection of our bid.

Site Visit /Understanding:

- We confirm that we have visited the site/clearly understood the requirements and expectations of the college authorities.

Scope of Work:

- We have thoroughly reviewed the scope of work mentioned in the bid document. The entire inventory/requirement/work has been verified and found to be in order. We also confirm that no additional items beyond the listed inventory/requirement will be required for successful completion of the work. However, if any additional item is required during execution, the same shall be provided by us as per the requirement.

Bidder Details

Name of Bidder: ______________________________________

Address: _____________________________________________

Contact Person: _______________________________________

Mobile No.: ___________________________________________

Email ID: _____________________________________________

Authorized Signatory: __________________________________

Signature & Stamp: ____________________________________

Date: _________________

Place: ________________

Commercial Bid: (in separate sealed envelope/password protected file via email)

# Bid for “SITC of chemical Earthing’s”

# (Tender No. : 2025-26/Estate/2B/LNM-1233)

| S.No. | DESCRIPTION OF ITEM (S) | UNIT | QTY | Rate | Amount |
| --- | --- | --- | --- | --- | --- |
| 1 | Supply, Installation, Testing & Commissioning of Chemical Earthing System (GI) - 3meter Length 50 mm Dia, With GEC. (Ground Enhancing Compound) | Nos | 9 |  |  |
| 2 | Construction of pit chamber: Brick masonry (450 mm) with cement plaster 12 mm thick with heavy duty earthing pit cover (GI / CI) with locking arrangement (size as per pit) | Nos | 9 |  |  |
| 3 | Supply & installation of GI strip 25 × 6 mm (from pit upto equipment / upto route) including saddles/clamps | Mtr | 150 |  |  |
| 4 | Earth Testing | Job | 206 |  |  |
| 5 | Paint work on earth chamber | Nos | 9 |  |  |
|  | Total |  |  |  |  |
|  | GST@18% |  |  |  |  |
|  | Grand Total |  |  |  |  |

GENERAL TERMS AND CONDITIONS:

- All applicable taxes such as GST must be clearly mentioned. If not specified, it shall be deemed that all such charges are included in the quoted price.

- If the supplier does not have a particular item or proposes a different make than that specified in the tender, the same must be clearly highlighted in the bid.

- Prices must be inclusive of all charges such as packing, forwarding, transit insurance, transportation, loading, unloading (up to 50 meters), installation, and any other incidental expenses.

- Bid must be submitted on an F.O.R. basis for delivery at: The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur – 302031.

- Bid shall remain valid for a minimum period of 30 days. No change in prices will be accepted during the validity period.

- The LNMIIT reserves the right to reject any quotation without assigning any reason.

- Payment terms shall be mutually decided and agreed upon between the Institute and the vendor.

- The bidder must submit a No Conflict of Interest Declaration along with the bid.

- The bid must be submitted on the company’s letterhead and in the LNMIIT-prescribed format only.

- Any item or service not being supplied by the bidder must be clearly mentioned separately in the bid.

- Vendors must provide a photocopy of their cheque/cancelled cheque along with the invoice for payment processing.

- Prices shall be quoted in Indian Rupees (INR) only.

- Total prices shall be quoted for the complete scope of work as per technical specifications, inclusive of all taxes, duties, insurance, packing, forwarding, and incidental charges.

- Agencies or individuals who are debarred or blacklisted are not permitted to participate in the tendering process. Any agency engaging a debarred person for negotiations or representation is also liable to be debarred.

- If the work is not completed within the stipulated time mentioned in the work order, the competent authority of LNMIIT reserves the right to accept partial work on suitable terms, cancel the supply/work order, withhold or stop payment, forfeit the Earnest Money Deposit, or debar the agency. The decision of the Competent Authority shall be final and binding.

- In case two or more bidders quote the same rates, the final selection shall be made through a draw of lots conducted by a committee comprising LNMIIT administrative members(PCC).

- Vendors are required to visit the site and conduct a detailed survey before submitting their bid to understand the exact requirements. No request for additional items or modifications will be entertained later.

- A pre-bid meeting and/or site visit may be arranged prior to submission of bids to clarify any doubts regarding project details, scope of work, and required documents.

Signature with seal