# Tender No:. 2025-26/ESTATE/2B/LNM-1234

The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “Servicing & Testing of 11 KV substation”. Bidders can submit their sealed offers/s at the following address by Email/Speed-Post/ Registered Post/ By-hand/courier before 05:00 PM on 09.01.2026 (Last date of bid submission).

Filing of Tender:

Option 1: Physical submission of offers (hard copy) in sealed envelopes.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the institute in person/ Speed-Post/ Registered Post/ By-hand/courier of the Institute after marking due entries in the Receipt Book available with the Security Officer at the main gate.

The tender subject and reference number must be mentioned on the envelope.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Option 2: Password-protected online submission via Email

Password-protected offers can be submitted by the bidders via email at the below-mentioned email IDs.

tender-document@lnmiit.ac.in (password-protected document)

tender-password@lnmiit.ac.in (password only)

The tender subject and reference number must be mentioned in the subject line of the emails.

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory, are required to be submitted in two separate envelopes/emails.

Envelopes/Emails should be duly marked as follows:

- Technical bid for the: Servicing & Testing of 11 KV substation (The technical bid must be submitted without password protection)

- Commercial Bid for the: Servicing & Testing of 11 KV substation (The commercial bid must be submitted with password protection.)

- Both Envelopes/files should be enclosed/attached in a single envelope/email bearing the heading “Bid for Servicing & Testing of 11 KV substation (Tender No. : 2025-26/Estate/2B/LNM-1234)”.

Bids are liable to be rejected:

- If the above-mentioned bid submission procedure is not followed.

- Incomplete and non-conforming bids.

- Arbitration: All disputes and differences arising between the two parties in connection with this order shall be mutually settled as far as possible, failing which, all such disputes shall be referred to arbitration and settlement under the provision of the Arbitration and Conciliation Act, 1996 and as amended from time to time or any such law for the time being prevailing in India. The venue of such arbitration shall be Jaipur.

Technical Bid: (in a separate sealed envelope/via email)

# Bid for Servicing & Testing of 11 KV substation

# (Tender No. : 2025-26/Estate/2B/LNM-1234)

Bidder is required to furnish the requisite details as per the below mentioned table format and proof of such documents to be uploaded along with the bid under respective title/ headings as mentioned at column no ‘C’ accordingly.

| S.No. | Title/ Heading Details sought by buyer | Details/ Certificate No. (Attached Y/N) |
| --- | --- | --- |
| A | B | C |
| 1. | Bidder Firm Name & Registration No, |  |
| 2. | Bidder’s Company profile or brief note |  |
| 3. | PAN Card No,. |  |
| 4. | GST Number |  |
| 5. | List of Directors/ Partners/Proprietor/ Members of the Bidder’s Firm |  |
| 6. | Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members |  |
| 7. | Bidder Turnover - Average annual turnover for last three years |  |
| 8. | The Client List with some purchase orders and satisfactory certificate (to whom the vendor has delivered the goods/provided the services in the past (Three (03) purchase orders/work orders, at least one from each of the last three years, including the previous year.) |  |
| 9. | If the bidder is authorized by the OEM/Manufacturer. Proof of the same is to be submitted with the Technical Bid |  |
| 10. | An undertaking (self-certificate) that the agency has not been blacklisted by a Central/State/UT Government Institutions and there has been no litigation with any government department/institution on account of any services/supplies. |  |
| 11. | Scanned copy of EMD/ Tender Fees paid through RTGS/NEFT (if required/asked in the tender) |  |
| 12 | Xerox copies of MoUs with previous colleges (minimum three) must be attached. (Applicable for student fest only). |  |

- Technical specification:

- Scope of work:

For Servicing, Testing & Maintenance of Transformer, HT/LT Panels, Capacitor Panels, ACB/VCB, Earthing & Other Electrical Systems

A. Servicing & Testing of Transformers (1000 kVA, 11kV/433V)

- Transformer Servicing Work

  - Physical inspection of transformer body, bushings, gaskets, radiator fins.

  - Checking of oil leakage, loose connections, earthing status.

  - Cleaning of external surfaces and tightening of all accessible terminations.

  - Verification of nameplate details and transformer rating.

- Oil Testing (BDV Value)

  - Collection of oil sample as per IS:6792.

  - BDV test using calibrated BDV test kit.

  - Submission of test report with observations and recommendations.

- Insulation Resistance Test

  - Meggering at 5kV between HV–LV, HV–Body, LV–Body.

  - Comparison with previous records and standard values.

- Winding Resistance Test

  - Resistance measurement of HV and LV windings using micro-ohm meter.

  - Identification of imbalance between phases.

- Logic Test / Functional Test

  - Verification of transformer control wiring logic.

  - Checking functionality of protection relays (OLTC interlocks if applicable).

- Oil Filtration

  - Filtration of transformer oil through high vacuum filtration machine.

  - Achieving desired BDV (>60 kV) and moisture level (<30 ppm).

- Transformer Oil Top-Up

  - Top-up of transformer oil as per requirement after filtration.

- Silica Gel Replacement

  - Replacement of silica gel breather.

  - Ensuring moisture-free indication (blue color).

B. HT Breaker Tests (Make ABB/CG)

- Breaker Timing Test

  - Opening/closing timing measurement using breaker analyzer.

  - Verification against OEM standards.

- Contact Resistance Test

  - Measurement of main contact resistance (mΩ range).

  - Identification of pitted/worn contacts.

- Relay Function Test

  - Functional testing of numerical or static relays.

  - Testing O/C, E/F, UV, OV protections.

  - Verification of trip circuits.

- Insulation Resistance Test

  - IR testing of breaker busbars, PT/CT circuits, control wiring.

C. Servicing of Substation Equipment

1. Servicing of ACBs (Make L&T/Legrand)

- Cleaning of arc chambers, poles, moving/fixed contacts.

- Lubrication of mechanical linkages and charging system.

- Testing of protection relays (O/L, S/C, E/F).

- Closing/opening coil test, spring charging motor test.

- Tightening of terminals and checking of interlocks.

2. Servicing of VCBs (Make ABB/CG)

- Cleaning and lubrication of mechanism.

- IR test and contact resistance measurement.

- Verification of closing/opening coil performance.

C. Servicing, Testing & Cleaning Work for Capacitor & LT Panels

- Servicing of Capacitor Panels

  - Cleaning of panels, capacitor banks, contactors, and relays.

  - Tightening of busbar connections and MCCBs.

  - Checking capacitor health (kVAR, temperature, bulging).

  - Checking APFC relay and step sequencing.

- Servicing of LT Panel (Domestic) – Full Preventive Maintenance

  - Cleaning of entire LT panel.

  - Tightening all cable lugs, busbar joints, switches, meters.

  - Functional checking of MCCBs, MCBs, timers, relays.

  - IR test of feeders and busbars.

- Servicing of LT Panel (Non-Domestic) – Full Preventive Maintenance

  - All activities as above with additional load-side monitoring.

  - Checking overcurrent/earth fault settings.

  - Thermal scanning after servicing.

D. Thermography of LT Panels

- Capacitor Panel Thermography

  - IR thermal scanning of live connections.

  - Identifying hot spots, loose connections, overheating components.

  - Submission of thermography report with images.

- LT Panel (Domestic)

  - Thermal scanning and detailed report.

- LT Panel (Non-Domestic)

  - Thermal scanning with identification of high-load feeders.

- Other Work:

- Earthing Testing

  - Earth resistance measurement using fall-of-potential method.

  - Report submission.

- Tightening of Wiring, Thimbles, Joints

  - Panel-wide tightening to avoid faults, heating, and breakdowns.

- Contactor 3P (18A/32A/63A) – 440V Coil

  - Replacement of worn-out contactors.

  - Coil voltage verification.

- ACB Front Fascia (L&T CN-CS 1600C)

- ACB Front Fascia Cover Seal (L&T CN-CS 1600C)

- ACB Trip Switch (L&T CN-CS 1600C)

  - Supply and installation.

  - Mechanical fitment and functional verification.

- MFM Meter Calibration

  - Calibration of multifunction meter with reference standard.

  - Confirmation of voltage, current, PF, frequency accuracy.

- Paint on Earthing Pit

  - Cleaning and applying anti-corrosion paint as per standard.

- DG Alternator Service

  - Cleaning, visual inspection, insulation test.

  - Bearing check, slip ring inspection.

  - Checking for heating, vibration, and rectifier circuit.

- Supply & Installation of MFM (Schneider EM1000)

- Installation with CT/PT, wiring, drilling, cutting.

- Configuration of meter parameters.

- Testing of communication and accura

- Indicators (R, Y, B, G)

- Supply and installation of panel indicators.

- Wiring and functional test.

- SAFETY PROCEDURES:

1. General Electrical Safety Requirements

- Only authorized and competent electricians/engineers shall work on the system.

- Valid PPE must be worn: arc-rated clothing, insulating gloves, safety shoes, helmet, face shield, goggles.

- Ensure Lockout–Tagout (LOTO) is applied before starting any work.

- Use only calibrated instruments (Megger, Tong Tester, BDV Kit, Thermal Scanner).

- Work area must be barricaded and signage such as "Work in Progress – Do Not Switch On" must be displayed.

2. Safety for Transformer Servicing & Testing

- Isolate the 11kV supply and ensure earthing discharge rods are applied.

- Test for absence of voltage on all terminals.

- Ensure transformer oil is handled carefully (flammable).

- Use proper gloves when handling silica gel or oil samples.

3. Safety for HT Breaker Servicing (ABB/CG)

- HT breakers must be racked out to the isolated, test position.

- Use insulated tools for busbar and CT/PT connection areas.

- Only trained personnel shall operate breaker truck mechanisms.

- Verify spring discharge and ensure "spring charged" indication is OFF before maintenance.

4. Safety for ACB/VCB Servicing

- Switch OFF incoming supply and apply LOTO.

- Discharge closing and tripping springs.

- Avoid touching arc chambers immediately after operation (hot).

- Use insulated mats around panel area.

5. Safety for LT Panel and Capacitor Panel Servicing

- Ensure panel is fully isolated before cleaning or tightening.

- Capacitors should be discharged for a minimum of 5–10 minutes before touching.

- Use safety goggles; capacitor banks may swell or burst if faulty.

6. Safety for Thermography

- Thermography is done on live equipment—keep a safe distance.

- Use appropriate insulating mats and gloves.

- Do not open doors of high-load or high-risk panels beyond safe limit.

7. Safety for Earthing Work

- Test earth pit in dry conditions to avoid inaccurate readings.

- Avoid touching metallic parts during testing.

- Ensure cables are not live during connections.

8. Safety for DG Alternator Service

- Ensure DG is completely shut down and cannot auto-start.

- Do not touch rotating parts immediately after stopping.

- Verify battery isolation.

| S. NO. | Particular | Make/Description | Qty | UOM |
| --- | --- | --- | --- | --- |
| A | Servicing & Testing of Transformers |  |  |  |
| 1 | Servicing of Transformer work | 1000KVA,11KV/433V | 3 | Job |
| 2 | Oil Testing(BDV Value) | 1000KVA,11KV/433V | 3 | Job |
| 3 | Insulation Resistance Test | 1000KVA,11KV/433V | 3 | Job |
| 4 | Winding Resistance Test | 1000KVA,11KV/433V | 3 | Job |
| 5 | Logic test | 1000KVA,11KV/433V | 3 | Job |
| 6 | Oil Filteration | 1000KVA,11KV/433V | 3 | Job |
| 7 | Transformer oil top up | AS Per req. | 200 | Ltr |
| 8 | 1kg sillica |  | 3 | Nos |
| B | HT Breaker Tests |  |  |  |
| 1 | Breaker Timing Test | Make ABB/CG | 4 | Job |
| 2 | Contact Resistance Test | Make ABB/CG | 4 | Job |
| 3 | Relay function Test | Make ABB/CG | 4 | Job |
| 4 | Insulation Resistance Test | Make ABB/CG | 4 | Job |
| C | Servicing of Substation equipment |  |  |  |
| 1 | Servicing of ACB's | Make L&T/Legrand | 22 | Job |
| 2 | Servicing of VCB's | Make ABB/CG | 4 | Job |
| C | Servicing, Testing & cleaning work for Capacitor & LT Panels |  |  |  |
| 1 | Servicing of Capacitor Panel |  | 3 | Job |
| 2 | Servicing of LT Panel(Domestic) Full Preventave Maintenance |  | 1 | Job |
| 3 | Servicing of LT Panel(Non-Domestic) Full Preventive Maintenance |  | 1 | Job |
| D | Thermography of LT Panels |  |  |  |
| 1 | Capacitor Panels |  | 3 | Job |
| 2 | LT Panel(Domestic) |  | 1 | Job |
| 3 | LT Panel(Non-Domestic) |  | 1 | Job |
| E | Capacitor |  |  |  |
| 1 | 10KVAR | Epcos/L&T | 2 | Nos |
| 2 | 15 KVAR | Epcos/L&T | 2 | Nos |
| 3 | 25 KVAR | Epcos/L&T | 4 | Nos |
| F | Supply & Installation of Service Parts |  |  |  |
| 1 | Under voltage relay,415V | Make L&T | 2 | Nos |
| 2 | Shunt release coil,415V | Make L&T | 2 | Nos |
| 3 | 6A fuse | Make L&T | 20 | Nos |
| 4 | Arc chute | Make L&T | 1 | Nos |
| 5 | Main Spring | Make L&T | 2 | Nos |
| 6 | Pole Assembly | Make L&T | 1 | Nos |
| G | Other Work |  |  |  |
| 1 | Earthing testing |  | 40 | Job |
| 2 | Tighting of Wiring,Thimbles,joints etc |  | 10 | Job |
| 3 | Contactor 3P 18A, 440V coil voltage |  | 1 | Nos |
| 4 | Contactor 3P 32A, 440V coil voltage |  | 1 | Nos |
| 5 | Contactor 3P 63A, 440V coil voltage |  | 1 | Nos |
| 6 | ACB Front Fascia | L&T CN-CS 1600C | 1 | Nos |
| 7 | ACB Front Fascia cover seal | L&T CN-CS 1600C | 2 | Nos |
| 8 | ACB Trip Switch | L&T CN-CS 1600C | 1 | Nos |
| 9 | MFM Meter Calibration |  | 10 | Job |
| 10 | Paint on Earthing pit |  | 30 | Job |
| 11 | DG alternator service |  | 3 | Job |
| 12 | Supply & Installation of MFM Power & Energy Meter EM1000 with suitable CT/PT, cutting drilling, wiring etc | Schnider EM1000 | 3 | Nos |
| 13 | Indicators R,Y,B,G |  | 100 | Nos |

Annexure

To Whomsoever It May Concern

This is to confirm that we, the undersigned, intend to participate in Tender No. : 2025-26/Estate/2B/LNM-1234 (Tender Number) for the tender/work titled: “Servicing & Testing of 11 KV substation” (Item Name)”

We hereby certify the following:

No Conflict of Interest:

- We declare that we have no conflict of interest in participating in the above tender. We further confirm that we are not engaged in any activity or association that may compromise, or be perceived to compromise, our impartiality or ability to fulfil the obligations of the tender.

Undertaking on Blacklisting & Litigation (Self-Certificate):

- We hereby undertake that:

- Our agency/firm has never been blacklisted or debarred by any Central Government, State Government, Union Territory administration, or any other Institution/Organization.

- There is no ongoing or past litigation against our agency/firm with any Central Government, State Government, Union Territory administration, or any other Institution/Organization on account of any services/supplies.

- If at any stage the above declaration is found to be false, the Institute shall have the right to take any action as deemed appropriate, including rejection of our bid.

Site Visit /Understanding:

- We confirm that we have visited the site/clearly understood the requirements and expectations of the college authorities.

Scope of Work:

- We have thoroughly reviewed the scope of work mentioned in the bid document. The entire inventory/requirement/work has been verified and found to be in order. We also confirm that no additional items beyond the listed inventory/requirement will be required for successful completion of the work. However, if any additional item is required during execution, the same shall be provided by us as per the requirement.

Bidder Details

Name of Bidder: ______________________________________

Address: _____________________________________________

Contact Person: _______________________________________

Mobile No.: ___________________________________________

Email ID: _____________________________________________

Authorized Signatory: __________________________________

Signature & Stamp: ____________________________________

Date: _________________

Place: ________________

Commercial Bid: (in separate sealed envelope/password protected file via email)

# Bid for Servicing & Testing of 11 KV substation

# (Tender No. : 2025-26/Estate/2B/LNM-1234)

| S. NO. | Particular | Make/Description | Qty | UOM | Rate | Amount |
| --- | --- | --- | --- | --- | --- | --- |
| A | Servicing & Testing of Transformers |  |  |  |  |  |
| 1 | Servicing of Transformer work | 1000KVA,11KV/433V | 3 | Job |  |  |
| 2 | Oil Testing(BDV Value) | 1000KVA,11KV/433V | 3 | Job |  |  |
| 3 | Insulation Resistance Test | 1000KVA,11KV/433V | 3 | Job |  |  |
| 4 | Winding Resistance Test | 1000KVA,11KV/433V | 3 | Job |  |  |
| 5 | Logic test | 1000KVA,11KV/433V | 3 | Job |  |  |
| 6 | Oil Filteration | 1000KVA,11KV/433V | 3 | Job |  |  |
| 7 | Transformer oil top up | AS Per req. | 200 | Ltr |  |  |
| 8 | 1kg sillica |  | 3 | Nos |  |  |
| B | HT Breaker Tests |  |  |  |  |  |
| 1 | Breaker Timing Test | Make ABB/CG | 4 | Job |  |  |
| 2 | Contact Resistance Test | Make ABB/CG | 4 | Job |  |  |
| 3 | Relay function Test | Make ABB/CG | 4 | Job |  |  |
| 4 | Insulation Resistance Test | Make ABB/CG | 4 | Job |  |  |
| C | Servicing of Substation equipment |  |  |  |  |  |
| 1 | Servicing of ACB's | Make L&T/Legrand | 22 | Job |  |  |
| 2 | Servicing of VCB's | Make ABB/CG | 4 | Job |  |  |
| C | Servicing, Testing & cleaning work for Capacitor & LT Panels |  |  |  |  |  |
| 1 | Servicing of Capacitor Panel |  | 3 | Job |  |  |
| 2 | Servicing of LT Panel(Domestic) Full Preventave Maintenance |  | 1 | Job |  |  |
| 3 | Servicing of LT Panel(Non-Domestic) Full Preventive Maintenance |  | 1 | Job |  |  |
| D | Thermography of LT Panels |  |  |  |  |  |
| 1 | Capacitor Panels |  | 3 | Job |  |  |
| 2 | LT Panel(Domestic) |  | 1 | Job |  |  |
| 3 | LT Panel(Non-Domestic) |  | 1 | Job |  |  |
| E | Capacitor |  |  |  |  |  |
| 1 | 10KVAR | Epcos/L&T | 2 | Nos |  |  |
| 2 | 15 KVAR | Epcos/L&T | 2 | Nos |  |  |
| 3 | 25 KVAR | Epcos/L&T | 4 | Nos |  |  |
| F | Supply & Installation of Service Parts |  |  |  |  |  |
| 1 | Under voltage relay,415V | Make L&T | 2 | Nos |  |  |
| 2 | Shunt release coil,415V | Make L&T | 2 | Nos |  |  |
| 3 | 6A fuse | Make L&T | 20 | Nos |  |  |
| 4 | Arc chute | Make L&T | 1 | Nos |  |  |
| 5 | Main Spring | Make L&T | 2 | Nos |  |  |
| 6 | Pole Assembly | Make L&T | 1 | Nos |  |  |
| G | Other Work |  |  |  |  |  |
| 1 | Earthing testing |  | 40 | Job |  |  |
| 2 | Tighting of Wiring,Thimbles,joints etc |  | 10 | Job |  |  |
| 3 | Contactor 3P 18A, 440V coil voltage |  | 1 | Nos |  |  |
| 4 | Contactor 3P 32A, 440V coil voltage |  | 1 | Nos |  |  |
| 5 | Contactor 3P 63A, 440V coil voltage |  | 1 | Nos |  |  |
| 6 | ACB Front Fascia | L&T CN-CS 1600C | 1 | Nos |  |  |
| 7 | ACB Front Fascia cover seal | L&T CN-CS 1600C | 2 | Nos |  |  |
| 8 | ACB Trip Switch | L&T CN-CS 1600C | 1 | Nos |  |  |
| 9 | MFM Meter Calibration |  | 10 | Job |  |  |
| 10 | Paint on Earthing pit |  | 30 | Job |  |  |
| 11 | DG alternator service |  | 3 | Job |  |  |
| 12 | Supply & Installation of MFM Power & Energy Meter EM1000 with suitable CT/PT, cutting drilling , wiring etc | Schnider EM1000 | 3 | Nos |  |  |
| 13 | Indicators R,Y,B,G |  | 100 | Nos |  |  |
| Amount |  |  |  |  |  |  |
| GST as Applicable |  |  |  |  |  |  |
| Amount Inclusive GST &Transportation |  |  |  |  |  |  |

GENERAL TERMS AND CONDITIONS:

- All applicable taxes such as GST must be clearly mentioned. If not specified, it shall be deemed that all such charges are included in the quoted price.

- If the supplier does not have a particular item or proposes a different make than that specified in the tender, the same must be clearly highlighted in the bid.

- Prices must be inclusive of all charges such as packing, forwarding, transit insurance, transportation, loading, unloading (up to 50 meters), installation, and any other incidental expenses.

- Bid must be submitted on an F.O.R. basis for delivery at: The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur – 302031.

- Bid shall remain valid for a minimum period of 30 days. No change in prices will be accepted during the validity period.

- The LNMIIT reserves the right to reject any quotation without assigning any reason.

- Payment terms shall be mutually decided and agreed upon between the Institute and the vendor.

- The bidder must submit a No Conflict of Interest Declaration along with the bid.

- The bid must be submitted on the company’s letterhead and in the LNMIIT-prescribed format only.

- Any item or service not being supplied by the bidder must be clearly mentioned separately in the bid.

- Vendors must provide a photocopy of their cheque/cancelled cheque along with the invoice for payment processing.

- Prices shall be quoted in Indian Rupees (INR) only.

- Total prices shall be quoted for the complete scope of work as per technical specifications, inclusive of all taxes, duties, insurance, packing, forwarding, and incidental charges.

- Agencies or individuals who are debarred or blacklisted are not permitted to participate in the tendering process. Any agency engaging a debarred person for negotiations or representation is also liable to be debarred.

- If the work is not completed within the stipulated time mentioned in the work order, the competent authority of LNMIIT reserves the right to accept partial work on suitable terms, cancel the supply/work order, withhold or stop payment, forfeit the Earnest Money Deposit, or debar the agency. The decision of the Competent Authority shall be final and binding.

- In case two or more bidders quote the same rates, the final selection shall be made through a draw of lots conducted by a committee comprising LNMIIT administrative members(PCC).

- Vendors are required to visit the site and conduct a detailed survey before submitting their bid to understand the exact requirements. No request for additional items or modifications will be entertained later.

- A pre-bid meeting and/or site visit may be arranged prior to submission of bids to clarify any doubts regarding project details, scope of work, and required documents.

Signature with seal