CORRIGENDUM

Name of Work: VRV/VRF Air Conditioning Machines Works for Boys Hostel -1 & Girls Hostel in University Campus.

Tender No.:2025-26/Estate/2B/LNM-1229
Date: 23/12/2025

This is to inform all prospective bidders that the following amendments/clarifications are hereby issued to the above-mentioned tender document. These shall be treated as part and parcel of the original tender.

- Earnest Money: EMD shall be ₹14 lakhs in place of ₹20 lakhs. (Refence of Page No. 3)

- Schedule of Quantities: Refer to S. No. A (Reference: Page No. 24)

  - Ambient Temperature shall be 55°C in place of 50°C

  - C.O.P.: Should be 3.7 to 4.0 at 100% load.

- Schedule of Quantities: Refer to S. No. A - 2 (a to f) (Reference: Page No. 24)

  - Indoor Hi-Wall Unit capacity should be read as in TR in place of HP.

  - Cordless Remote Controllers: Qty.: 50 Nos. for indoor units; individual remote for each unit not required.

- Schedule of Quantities: Refer to S. No. 3 (Reference: Page No. 24): Centralized Remote-Control System: Qty.: 3 Nos. (in place of RO).

- Schedule of Quantities: Refer to S. No. B - 2 (a to f) (Reference: Page No. 24 & 25)

  - Indoor Hi-Wall Unit capacity should be read as in TR in place of HP.

- Price Bid (S. No. A, Page 32): Delete make Blue Star; add Carrier.

- Price of Bid: Refer to S. No. A - 2 (a to f) (Reference: Page No. 32 & 33)

  - Indoor Hi-Wall Unit capacity should be read as in TR in place of HP.

- Price Bid: Refer to S. No. A_ 3 (Reference: Page No. 33): Centralized Remote-Control System: Qty.: 3 Nos. (in place of RO).

- Price of Bid: Refer to S. No. B - 2 (a to f) (Reference: Page No. 33)

  - Indoor Hi-Wall Unit capacity should be read as in TR in place of HP.

- Added Points:

- Technical Data Sheet for VRV/VRF Indoor and Outdoor units must be provided by all Vendors, it should be part of the technical bid.

- Relative Humidity (RH): Summer: 75% and Monsoon: 65%