THE PROPOSED CONSTRUCTION

OF

LNMIIT INTERNATIONAL CENTRE FOR ARTIFICIAL INTELLIGENCE

TENDER DOCUMENT

FOR

SOLAR PV WORKS

THE LNM INSTITUTE OF INFORMATION TECHNOLOGY,

RUPA KI NANGAL, VIA JAMDOLI, JAIPUR, RAJASTHAN.

Index

| Sno. | Description | Page No. |
| --- | --- | --- |
| 1. | Notice Inviting Tender | 3 |
| 2. | Instruction to bidders | 4 |
| 3. | Eligibility Criteria | 6 |
| 4. | Scope of work | 10 |
| 5. | General Terms & Conditions | 13 |
| 6. | Technical Specifications for Solar PV Works | 17 |
| 7. | List of Approved makes | 38 |
| 8. | Schedule of quantities | 39 |
| 9. | Affidavit | 45 |
| 10. | Proforma EMD/ Performance bank guarantee/ Security deposit | 46 |
| 11. | Price bid | 49 |

Notice Inviting Bid

(Competitive bidding)

NIT no.: LICAI/NIT/009

The Director on behalf of THE LNM INSTITUTE OF INFORMATION TECHNOLOGY, JAIPUR (“LNMIIT”) having its office at Rupa ki Nangal, Via Jamdoli, Jaipur invites Item rate tender from Eligible firms/agencies for the following works thru online/hard copy submission under two bid system:

Name of the Project: Construction of LNMIIT International Centre for Artificial intelligence (LICAI) (G+5) at Jaipur.

Sub Head: Solar PV Works.

Detail of the Tender bid:

Earnest Money: Rs. 700000

Period of Completion: 2 Months.

Mobilization time - Nil

Revised Date of Issue of Bid: 16.02.2026

Date & Time of Pre-Bid Meeting: to be decided mutually.

Revised Last date & time of submission of bid document: 20.02.2026

Name: Dr. Kamal Kishore Khatri (Chairman-PCC)

Phone No.: 0141-3526101

Email id: chairman.pcc-projects@lnmiit.ac.in

Director

LNMIIT

Instructions for the Bidder

- This Notice Inviting Tenders (Part-1,2,3 & 4) i.e. Eligibility criteria for the bidder, Scope of work, Terms & conditions, Comprehensive warranty, Defects liability period, Comprehensive Maintenance for 5 years, General terms & conditions, General technical conditions, technical specifications, List of approved makes, Affidavit, Proforma for Bank guarantee, Price bid & Drawings shall form the TENDER DOCUMENTS.

- Filing of Tender:

Option 1: Physical submission of offers (hard copy) in sealed envelopes.

The bid document shall be submitted in two envelopes consisting of the following:

Envelope 1: Bid document duly signed and stamped by the authorised signatory along with the EMD as specified.

Envelope :2: Price Bid.

Price bid envelope i.e envelope 2 will be opened only of those bidders who successfully meet the eligibility criteria.

Option 2: Password-protected online submission via Email

Technical bid (without password) and Financial Bid (password protected) can be submitted by the bidders via email at the below-mentioned email IDs.

tender-document@lnmiit.ac.in (Bid document-Technical Bid and Financial bid)

chairman.pcc-projects@lnmiit.ac.in (password of Financial bid)

The tender subject and reference number must be mentioned in the subject line of the emails.

- The Contractors are to pay the amount of earnest money as specified in the tender notice separately along with the Tender. Tenders for which earnest money deposit has not been received separately shall be returned unopened/not to be considered for further processing.

- The Contractor should certify that he has studied the Work at site and acquainted himself with the position regarding construction, materials & labour required for the work.

- Should the Contractor notice any discrepancy or error in any statement made, he shall immediately bring to the notice of the LNMIIT-Project Manager of LNMIIT, Jaipur (project.manager@lnmiit.ac.in) and obtain clarifications before submitting the tender.  The tender shall be recorded as such in the covering letter to the tender, failing which the Owner shall have right to ask the Contractor to execute the Work according to the statement made in the tender, without any compensation.

- The Rates should be quoted in figures and words, and the respective amounts or total shall be given by each TENDERER. In case of any difference in rates in figures / words, those given in words, shall hold good as quoted rate and in case of any difference in rates and Total amount, quoted Rates shall hold good.

- The TENDERS shall remain valid for acceptance for 30 days from the last date of Submission.

- The successful TENDERER shall be intimated about the Award of Work and the Earnest Money Deposits of other TENDERERS shall be returned without any interest on the amount deposited.

- The LNMIIT reserves the right to reject any / all TENDERS without assigning any reason and shall not be bound to accept the lowest or any other TENDER.

- TENDER not accompanied by the requisite EARNEST MONEY DEPOSIT in the specified form or accompanied with the conditional offer are liable to be summarily rejected.

- The Bidder should stamp and sign the document in order to ascertain that he complies with all the specifications and terms and conditions mentioned in the Bid.

- Earnest money deposit will be paid online or thru Demand draft to the following bank account:

Account Name         : “ The LNM Institute of Information Technology”

Account No.     :       001201038168

Bank                    :       ICICI Bank Ltd.

Branch         :     C-Scheme, Jaipur

IFSC Code     :       ICIC0000012

Account type    :       Saving account

The acknowledgement of the EMD should be mailed to the finance officer on the email: finance@lnmiit.ac.in.

- Co-ordination with other agencies / contractors appointed directly by the owner:

The Successful bidder shall co-ordinate and provide facilities for the contractors appointed by the LNMIIT.

In addition to the above Clauses all requirements will have to be implemented by the Bidder for all persons employed by him working on the Site including monitoring to ensure implementation etc., employed directly by the Owner.

- The tender of any Contractor not complying with any of the above instructions 1 to 12 may be rejected.

I / We have carefully read the above said instructions have understood the same and shall comply with the same.

Place : 							Signature of the Contractor

Date:								With seal & address

Name of the Contractor: -

Contact No.

e-mail id:

Part-1

Eligibility Criteria for the bidder (Authorized dealer of the Solar PV Manufacturer) and the OEM (Solar PV Manufacturer)

| Sno. | Parameter | Documents to be submitted by Bidder |
| --- | --- | --- |
| 1 | Earnest Money Deposit: | The bidder should submit and EMD of Rs. 700000only |
| 2. | Bidder Turnover | The Bidder should submit the CA Certified turnover document for the Financial Turnover of Bidder for last three Financial Years i.e FY 2022-23, 2023-24 2024-25 . |
| 3. | OEM/Solar PV Manufacturer Turnover | The OEM should submit the CA Certified turnover document for the Financial Turnover of Bidder for last three Financial Years i.e FY 2022-23, 2023-24 2024-25 |
| 4. | OEM Authorized Certificate | The Bidder should submit the valid Bid specific OEM Authorization Certificate. The Authorization Certificate should clearly mention the Bid Number. Note: In case the Bidder itself is OEM, then the Bidder shall submit an undertaking whereby the bidder declares itself is OEM on his letterhead duly signed and stamped |
| 5. | Experience criteria & Past performance for the bidder | To qualify, each bidder should have supplied/ executed similar category product/ work i.e SITC of the Solar PV s in any Govt. Department/ PSU/ Public Listed Company in last five years with: One works of minimum value of Rs. --50000000-----------/- Or Two works of minimum value of Rs. -----30000000-------/- Requirements: - Completion certificates mentioning order number and order value issued by the relevant competent Authority |
| 6. | Experience Criteria & Past Performance for the OEM/D. G Set manufacturer ( 15 Years ) | The OEM shall have manufacturing experience of Solar PV s for a minimum of 15 years. The Bidder should submit valid documentary evidence in support of same. |
| 7. | Necessary Qualifying Criteria for OEM/ Solar PV Manufacturer | To qualify, the OEM/ Solar PV Manufacturer should comply with the following conditions: 1) Manufacturing and Testing Facility, R&D Centre and dedicated training center to train its personnel in India. 2) Domestic Production capacity of the factory in India shall not be less than 1000 Solar PV s per anum. 3) The Manufacturer shall have Service Centers in at least 25 Nos town/cities including at least 15 Nos state capitals in India. 4) The Solar PV Manufacturer shall furnish an undertaking regarding availability of spares for entire life of the Solar PV s i.e 15 to 20 years 5) The Solar PV Manufacturer shall furnish an undertaking that: a) Solar PV tests and safety features confirms to relevant updated Indian standards b) Quality standards shall confirm to IS/ISO— 9001:2015 c) The Fire Rating of the Solar PV s shall be as per National Building Code-2016 d) The downtime of the Solar PV shall not be more than 8 hrs (average) in case of minor faults and 7 days (average) in case of major faults. 6) Details of Tollfree Number, Emai-Id for lodging complaints shall be provided. |
| 8. | GST number | The bidder should attach GST number detail mandatorily |
| 9. | PAN Card | The bidder should attach PAN card detail mandatorily |
| 10. | Make in India Certificate ( MII ) | The Bidder should submit the Make in India Certificate in the Letter head duly signed and stamped |
| 11. | BOQ Compliance | The Bidder should stamp and sign the document in order to ascertain that he complies all the specifications and terms and conditions mentioned in the Bid |
| 12. | Location of the nearest Service Centre | The Bidder has to provide the Address of the Service Centre along with Contact Number |
| 13. | ISO 9001:2015 Certificate | The Bidder should submit the valid ISO 9001:2015 Certificate of the Bidder/OEM |
| 14. | Affidavit as per Annexure-1 | The Bidder should submit the Affidavit as per Annexure-1 |

Part-2

Scope of Work:

- This work covers supplying, testing & commissioning of transformers including coordinating with the installation team for its installation including panels etc. complete, all preparatory work & putting into operation of Solar PV s including comprehensive maintenance for 5 years including one year of defects liability period.

- Location: The work shall be carried out in the Building of LNMIIT International Centre for Artificial intelligence (LICAI) (G+5) at Jaipur

- The work shall be executed as per CPWD General Specifications for Solar PV works, Part-VII 2013, as amended upto date and as per directions of Project manager. These additional specifications/ conditions are to be read in conjunction with above and in case of variations; specifications given in these additional conditions shall apply. However, nothing extra shall be paid on account of these additional specifications and conditions, as the same are to be read along with the schedule of quantities for the work.

- The tenderer should in his own interest visit the site and get familiarized with the site conditions before tendering.

- The work shall comprise of entire labour including supervision and all materials necessary to make a complete installation and such tests and adjustments and commissioning as may be required by the department. The term complete installation shall not only mean major items of the plant and equipment’s covered by specifications but all incidental sundry components necessary for complete execution and satisfactory performance of installation with all layout charts whether or not those have been mentioned in details in the tender document in connection with this contract.

- All debris/Malba resulting due to work shall be removed on daily basis and completion of the work shall only be accepted after the site has been cleaned of all malba.In case contractor fails to comply the same shall be got removed by the other agency at the payment shall be recovered from the bill of the contractor.

- Minor building works necessary for installation of equipment’s, foundation, making of opening in walls or in floor and restoring to their original conditions, finish and necessary grouting etc. as required.

- The contractor shall be bound to execute such additional items which can be termed as logical, essential and necessary (even though not listed in schedule of work) for the effective execution of the work in totality.

- Maintenance (routine and preventive) DLP for one year from date of completion and handing over to department/Client.

- Inspection and testing: All routine tests confirming to be relevant shall be carried out and the test reports shall be submitted to Project Manager. The copies of all documents of routine and type test certificates of the equipment, carried out at the manufacturer’s premises shall be furnished to the Project Manager and consignee at the time of delivery of material at site. After completion of the work in all respects the contractor shall offer the installation for testing and operation.

12) COMPLIANCE WITH REGULATIONS AND INDIAN STANDARDS: All works shall be carried out in accordance with relevant regulation both statutory and those specified by the Indian Standards related to the works covered by this specification. In particular, the equipment and installation will comply with the following:

(i) 	BS: 5514 Specification for reciprocating internal combustion engine.

(ii) 	BS:5000 Rotating electrical machines of particular type or for particular applications.

(iii) 	IS: 1239 (Part-I & II) : Mild steel tubes and fittings

(iv) 	IS: 1651: Stationary cells and batteries lead acid type (with tubular positive plates).

(v) 	IS: 9224: Specification of low voltage fuses, General purpose.

(vi) 	IS: 4540: Mono-crystalline semi-conductor rectifier assemblies and equipment.

(vii)	IS: 5: Colours for ready mixed paints.

(viii)	IS: 4722: Rotating electrical machines

(ix)	IS: 1248: Specification for electrical indicating instruments.

(x)	IS: 10000: Methods of tests for internal combustion engines.

(xi)	IS: 10002: Specifications for performance requirements for constant speed

compression ignition (Diesel) engine for general purposes (above 20 KW)

(xii)	IS: 2147 : Degree of protection provided by enclosure for low voltage switchgear and control gear.

(xiii)	IS: 1600 : Code for type testing of constant speed IC engines for general purposes.

(xiv)	IS: 1601 : Performance of constant speed IC engines for general purposes.

xv)	ASME Power : Internal combustion engines.

(xvi)	Test Code PTC-17 : Codes of Diesel Engine Manufacturer's Association U.S.A

13)	Installation:

The installation work shall conform to Indian Electricity act and Indian Electricity Rules as amended upto the date of installation. The fuel oil installation shall meet all statutory requirements of Govt. of India as amended up to the date of installation. Any approval required from statutory authorities shall be obtained by the contractor. Nothing in this specification shall not be the limiting factor to relieve the contractor of their responsibilities.

The equipment’s furnished under this specification have to operate in a tropical climate and shall be given tropical and fungicidal treatment as per relevant specification.

13) Maintenance:

a. Sufficient trained and experienced staff & Engineer shall be made available to meet any exigency of work during the guarantee period of one year from the handing over of the installation.

b. Routine as well as preventive maintenance for one year from the date of taking over the installation shall be carried out and the record of the same shall have to be maintained.

c. Comprehensive maintenance period of 5 years for the successful bidder will begin after the handover of the work completing DLP.

14) Training:

The scope of the work includes on-the-job technical training of two persons at site. Nothing extra shall be payable on this account.

15)  Test Certificate:

As regards the type tests in case these have been done earlier by OEM for similar design/ type, same if produce shall be acceptable. In case, same is not done earlier, these will have to be done for one of the transformers of the present lot.

Part-3	Terms & Conditions for comprehensive warranty/defects liability period of one year and comprehensive maintenance for 5 years.

1) The Contractor shall regularly examine, lubricate and adjust the equipment and generally carry out planned maintenance in a systematic and controlled manner.

2) The Contractor shall repair or replace any parts detail which are found to be defective.

3)  All equipment covered in the contract are included in the comprehensive maintenance.

4) The contractor will assign a representative who will periodically visit the site once a month and will be available for consultation in any matter relating to the maintenance of Solar PV.

5) The work shall be carried out as General Specifications for Solar PV s-2013, Part-VII and amended upto date and the entire satisfaction of the Project manager.

6) The tendered rates shall be deemed to include all services covered under this contract and no extra payment will be made on this account.

7) Any accident that occurred due to negligence will be the entire responsibility of the contractor.

8) The time allotted for attending the complaints is 24 Hours and if the complaints are not done within 24 hours of the registration, a recovery @ Rs. 500/- per day shall be made against the contractor.

Part-4

General Terms & Conditions

1)  The intending bidder must read the terms and conditions of the bid carefully. He should only submit his bid if he considers himself eligible and he is in possession of all the documents required.

2) Information and Instructions for bidders posted shall form part of bid document.

3) The LNMIIT-Jaipur reserves the right to reject any prospective bid at any point of time, if the documents provided by the bidder appear to be fake or any false information is provided by the bidder.

4) The intending contractor is advised to visit the site of work, of his own, to acquainting himself regarding site details etc. prior to quoting the tender.

5) The time allowed for carrying out the work will be 90 days from the date of the contract order. If the Bidder fails to complete the work within 90 days from the date of contract order and the reason for delay is not found reasonable by the Project Manager, LNMIIT, he will be charged with @ Rs 5000/- per week. No fine will be imposed if the reason for the delay is found reasonable by the Project Manager.

6) Payment Terms:

a)  Serial no. “1.” of the Price bid: 75% of the quoted cost will be paid to the Bidder on the successful delivery of the Material at site. The remaining 25% of the quoted cost will paid after successful testing and commissioning.

b) Serial No. 2 of the Price bid : Payment to the bidder for this stage shall be as follows:

| Sno. | Payment schedule | % (Percent) |
| --- | --- | --- |
| 1 | 1st Year | 10.0 |
| 2 | 2nd Year | 15.0 |
| 3 | 3rd Year | 20.0 |
| 4 | 4th Year | 25.0 |
| 5 | 5th Year | 30.0 |

7) Intending bidders are advised to inspect and examine the site and its surroundings and satisfy themselves before submitting their bids as to the nature of the ground and sub-soil (so far as is practicable), the form and nature of the site, the means of access to the site, the accommodation they may require and in general shall themselves obtain all necessary information as to risks, contingencies and other circumstances which may influence or affect their bid. The bidder shall be deemed to have full knowledge of the site whether he inspects it or not and no extra charge consequent on any misunderstanding or otherwise shall be allowed. The bidders shall be responsible for arranging and maintaining at his own cost all.

8) It is required that each Bidder/Contractor (including their respective officers, employees and agents) adhere to the highest ethical standards, and report to the Director-LNMIIT all suspected acts of fraud or corruption or Coercion or Collusion of which it has knowledge or becomes aware, during the tendering process and throughout the negotiation or award of a contract.

9) Performance Guarantee:

a) The contractor whose bid is accepted will be required to furnish a performance guarantee of 5% (Five Percent) (Serial no. “1.” of the Price bid ) of the bid amount valid for 12 months from the date of contract order within 20 days of the issuing of contract order. This guarantee shall be in the prescribed form mentioned in the Bid document. The performance Guarantee shall be released 12 months after date of contract order.

b) In addition to the above the successful bidder should furnish a performance guarantee of 5% (Five percent) of bid amount (Serial No. 2 of the Price bid ) prior to the commencement of the comprehensive maintenance period of 5 years valid for 66 months. This comprehensive maintenance period will begin after the successful handover of the work.

The performance Guarantee in respect to AMC will be released after 45 days from the completion of the AMC Period.

This guarantee shall be in the form of Insurance Surety Bonds, Account Payee Demand Draft, Fixed Deposit Receipt or Bank Guarantee from any of the Commercial banks in accordance with the prescribed form as provided in the bid. In case, the Bidder fails to deposit the said Performance Guarantee within the period as mentioned above including the extended period, if any, the Earnest Money deposited by the Bidder shall be forfeited automatically without any notice to the Bidder. The earnest money deposited along with the bid shall be returned after receiving the aforesaid performance guarantee.

10) Rates: The rates quoted by the tenderer, shall be firm and inclusive of all taxes (including works GST, labour cess), duties, levies, octrori etc. and all charges for packing forwarding, insurance, freight and delivery, installation, testing, commissioning etc. at site including temporary construction of storage, risks overhead charges, general liabilities/obligations and clearance required if any.

11) The Contractor has to carry out comprehensive, routine and preventive maintenance as per manufacturer’s standard for a period of 12 months from the date of handing over. Nothing extra shall be paid on this account.

12) GUARANTEE: All equipment’s shall be guaranteed for a period of 12 months, from the date of taking over the installation by the department/Client against unsatisfactory performance and/or breakdown due to defective design, workmanship or material. The equipment or components, or any part thereof, found defective during guarantee period shall be forthwith repaired or replaced free of cost, to the satisfaction of the Project Manager. In case it is felt by the department that undue delay is being caused by the contractor in doing this, the same will be got done by the department at the risk and cost of the contractor. The decision of the Project manager in this regard shall be final & binding on the contractor.

13) The successful tenderer should furnish well in advance three copies of detailed instructions and manuals of manufacturers for all items of equipment’s regarding installation, adjustments, operation and maintenance i/c preventive maintenance and troubleshooting together with all the relevant data sheets, spare parts, catalogue and workshop procedure for repairs, assembly and adjustments etc all in triplicate.

14)   Dispute Resolution: If any dispute with regard to the terms of this Contract shall be handled through Arbitration, as per the following terms, between them:

(I) THAT, the parties agree that any dispute or difference whatsoever arising between them out of/under or in connection with or relating to the existence, meaning, scope, validity, termination, breach, or any other effect flowing from the Contract shall be referred to a Sole Arbitrator, as appointed under clause (IV) herein below;

(II) AND THAT, the parties agree that in respect of those matters, as are not defined in the terms and conditions of this Dispute Resolution Clause, or anywhere else in the Contract, the same shall be decided and settled by the Sole Arbitrator, in accordance with the Arbitration and Conciliation Act, 1996 and the amendments thereof as in operation on the date of execution of the Contract;

(III) AND THAT, the parties agree that the place of Arbitration shall be at Jaipur, Rajasthan;

(IV) AND THAT, whenever the parties decide to resort/resolve to Arbitration for dispute

resolution, the Director, LNMIIT shall be the authority to appoint the Sole Arbitrator and such appointment shall be binding on both the parties:

Provided that before approaching Director-LNMIIT for appointment of Sole Arbitrator, the parties shall make a sincere attempt to resolve their dispute, within a time period of 3 months, through mutual conciliation/ negotiations. The sole arbitrator shall not be an employee of any of the party to this tender.

(V) AND THAT all costs relating to the Arbitration proceedings shall be borne equally by both parties.

(VI) AND THAT, the parties agree that the language for making all submissions and evidence will be presented in ENGLISH during the proceedings.

(VII) AND THAT, it is agreed between the parties that they shall extend their fullest support and co-operation to the Sole Arbitrator and not seek adjournment of the Arbitration proceedings, without explaining the reasons therefore, in writing, in advance, for seeking of such adjournment, and further that there shall not be more than two such adjournments granted, even when there exists a valid reason for seeking such adjournment. And, it is further agreed that the parties should cooperate in completing the arbitration process and the broader dispute resolution within 6 months or at most with an extension, on mutual consent, of another 6 months;

(VIII) The sole Arbitrator shall record, in writing, the arguments of the two parties on each of the points of dispute and pass a reasoned and speaking Award thereon, within the Terms and Conditions of the Contract Agreement.

(IX) If any difference remains after an Arbitral award, and an appeal could be raised under the Arbitration and Conciliation Act, 1996, the appropriate Court within the Jaipur , Rajasthan shall deal with the matter.

TECHNICAL SPECIFICATIONS –Solar PV Works

Supply, Installation, Testing & Commissioning of Grid interactive Roof Top Solar Power Generation system at international center for Artificial Intelligence at LNMIIT, JAIPUR, including operation and comprehensive maintenance for Five years.

# Photovoltaic Modules:

  - Standards and Codes

Photovoltaic Modules shall comply with the following standards and codes.

| Standard | Description |
| --- | --- |
| IEC 61215-1:2021 RLV | Terrestrial photovoltaic (PV) modules - Design qualification and type approval - Part 1: Test requirements |
| IEC 61215-1-1:2021 RLV | Terrestrial photovoltaic (PV) modules - Design qualification and type approval - Part 1-1: Special requirements for testing of crystalline silicon photovoltaic (PV) modules |
| IEC 61730-1:2016 | Photovoltaic (PV) module safety qualification - Part 1: Requirements for construction |
| IEC 61730-2:2016 RLV | Photovoltaic (PV) module safety qualification - Part 2: Requirements for testing |
| IEC 61701:2020 | Photovoltaic (PV) modules - Salt mist corrosion testing |
| IEC TS 62804-1:2015 | Photovoltaic (PV) modules - Test methods for the detection of potential-induced degradation - Part 1: Crystalline silicon |

  - Technical Requirements

| Parameter |  |
| --- | --- |
| Cell/ Module Technology | Framed Dual Glass Bifacial module (N Type) |
| Module Efficiency | ≥ 22% (equal to or greater than 22%) |
| Rated power at STC | No negative tolerance is allowed |
| Temperature co-efficient of power | Not less than-0.40%/°C |
| Application Class as per IEC 61730 | Class A |

PV modules should be made in India and all the PV modules should be identical       (same model number) from the same manufacturer.

The glass panel of the modules shall be toughened low iron glass with a minimum thickness of 2 mm Low Iron ARC semi-tempered glass. The glass shall have an anti-reflective coating for better transmission and light absorption.

The back glass of the modules shall be 2 mm Low Iron Printed semi-tempered glass

The encapsulant used for the PV modules should be UV resistant and PID resistant in nature. No yellowing of the encapsulant with prolonged exposure shall occur. The encapsulant shall have the following properties.

The sealant used for edge sealing of PV modules shall have excellent moisture ingress protection with good electrical insulation (Break down voltage >15 kV/ mm) and with good adhesion strength. Edge tapes for sealing are not allowed.

The module frame shall be made of anodized aluminium, which should be electrically & chemically compatible with the module mounting structure.

IP68 UV resistant junction boxes with minimum 3-numbers of bypass diodes and 2-numbers of IEC 62852/ EN 50521 certified MC4 connectors with EN 50618 compliant 4 sq.mm copper cable shall be provided.

Modules must bear an RF identification tag inside the module lamination. The tag should contain the following information. RFID scanner and database of all the modules shall also be provided.

- Name of the manufacturer of the PV module

- Name of the manufacturer of Solar Cells.

- Month & year of the manufacture (separate for solar cells and modules)

- Country of origin (separately for solar cells and module)

- I-V curve for the module peak Wattage, Im, Vm and FF for the module

- Unique Serial No and Model No of the module

- Date and year of obtaining IEC PV module qualification certificate.

- Name of the test lab issuing IEC certificate.

- Other relevant information on traceability of solar cells and module as per ISO 9001 and ISO 14001.

Solar Modules should bear the BIS mark as notified by the Ministry of New and Renewable Energy (MNRE), Government of India.

# MODULE MOUNTING STRUCTURE (MMS):

Solar modules must be mounted on a stable, durable structure that can support  the arrays and withstand wind, rain, and other adverse conditions.

The module mounting structures shall have adequate strength and appropriate design suitable to climatic conditions of JAIPUR in all seasons, which can withstand the load and high wind velocities.

Refer drawings, part of installation which are coming in roof top installation with structure less than 1 mtr. height supports, strengthen as per structure design which also the scope of this tender.

Part of installation which are coming in roof top installation with structure tentative 4.65 mtr. height supports, strengthen as per structure design which also the scope of this tender.

Part of installation which are coming in roof top installation with structure tentative 9.17 mtr. height supports, strengthen as per structure design which also the scope of this tender.

Catwalk to be provided for solar pv maintenance for installation more than a man height level.

MMS will be designed keeping several structural considerations such as:

  - Load of the SPV installation.

  - Load bearing capacity of the terrace/ building truss.

  - Maximum wind loads at the project site, also factoring the height of the installation.

  - Seismic safety factors.

The materials used for structures shall be Hot dip Galvanized Mild Steel conforming to IS 2062. Minimum thickness of the galvanization shall be 80 Microns.

The Bolts, Nuts, fasteners and clamps used for panel mounting shall be of Stainless-Steel SS 304.

A sufficient gap should be provided between the rows to avoid the falling shadow  of one row on the next row.

No welding is allowed on the mounting structure except base plate to columns.

Each structure should have angle of inclination as per the site conditions to take maximum insolation.

Modules shall be clamped or bolted with the structure properly. The material of clamps shall be Al/ SS having weather resistant properties. Clamp/ bolt shall have EPDM rubber washer and shall be designed in such a way so as not to cast any shadow on the active part of a module.

It may be ensured that the design has been certified by a recognized Lab/ Institution in this regard and further by consultant & engineer-in-charge’s.

Each PV panel structure shall incorporate one bird repellent spike at a level higher than the panel upper edge. The location of the spike should be selected for minimum shadow effect.

The structures should be designed to allow easy replacement of any module. The array structure should be so designed that it will occupy minimum space without sacrificing the output from the SPV panels.

The Module mounting structures should be installed on the existing columns or trellis as   shown in the drawings. Contractor to ensure that in no case, waterproofing layer/ roof insulation should be damaged.

# String Inverter/ Power Conditioning Unit:

  - Code and standards

| Standard | Description |
| --- | --- |
| IEC 61683: 1999 | Photovoltaic systems–Power conditioners– Procedure for measuring efficiency |
| IEC 62109-1: 2020 | Safety of power converters for use in photovoltaic power systems – Part 1: General requirements |
| IEC 62109-2: 2021 | Safety of power converters for use in photovoltaic power systems – Part 2: Particular requirements for inverters |
| IEC 61000-6-1:2016 RLV | Electromagnetic compatibility (EMC) - Part 6-1: Generic standards - Immunity standard for residential, commercial and light-industrial environments |
| IEC 61000-6-8:2020 | Electromagnetic compatibility (EMC) - Part 6-8: Generic standards - Emission standard for professional equipment in commercial and light- industrial locations |
| IEC 62116:2014 | Utility-interconnected photovoltaic inverters – Test procedure of islanding prevention measures |
| IEC 60068-2-1:2007 | Environmental testing – Part 2-1: Tests – Test A: Cold |
| IEC 60068-2-2:2007 | Environmental testing – Part 2-2: Tests – Test B: Dry heat |
| IEC60068-2-14:2009 | Environmental testing – Part 2-14: Tests – Test N: Change of temperature |
| IEC 60068-2-30:2005 | Environmental testing - Part 2-30: Tests - Test Db: Damp heat, cyclic (12 h + 12 h cycle) |

PCU/ Inverter vendor (OEM) should be of reputed make and should have supplied a minimum 5 GW capacity globally or 500 MW in India during the past 5 years. Supporting documents in respect of the same shall be submitted with technical particulars/ data sheets of the PCU/ inverter for approval of consultant & engineer-in-charge’s.

# Technical requirements

| Rated power | As per design |
| --- | --- |
| Max. input voltage | 1000 V |
| Rated AC output voltage | 415 V (+/-10%), 3 Phase, 50 Hz |
| Rated frequency | 50 Hz |
| Grid Frequency Synchronization range | +/- 5 Hz |
| Power factor control range | 0.9 lag to 0.9 lead |
| Peak efficiency | >97% |
| Maximum loss in Sleep Mode | 0.05% of rated AC power |
| THD | Less than 3% at 100% load |
| IP Class | IP 65 |
| Switching devices | IGBT/ MOSFET |
| Control | Microprocessor /DSP |
| Ambient temperature | -20ºC to 50ºC |
| Humidity | 0-100 % |
| Grid Voltage tolerance | -0.20, +.15 |

Construction:

The PCU shall be suitable for climatic conditions prevailing at JAIPUR, RAJASTHAN in all seasons.

The rated AC capacity of the power conditioning unit/ string inverter shall be at 50°C.

PCU shall consist of a 3-phase inverter along with associated control, protection, filtering, measurement and data logging devices.

Every DC input terminal of PCU shall be provided with fuse/ MCB/ MCCB of appropriate rating. The combined DC feeder shall have appropriate isolators for safe start-up and shut down of the system. One spare DC input terminal shall be provided for each PCU.

Type-2 SPD conforming to IEC 61643-31 shall be provided between positive/ negative bus and earth on DC side and Type-2 SPD conforming to IEC 61643-11 shall be provided on AC side.

PCU shall have Circuit Breaker or Relay of appropriate rating at the output to isolate it from the grid in case of faults.

PCU shall have suitable numbers of MPPTs to maximize energy drawn from the PV array. The MPPT voltage range shall be sufficient enough to accommodate the  output voltage of the PV array at extreme temperatures prevailing at site.

The PCU output shall always follow the grid in terms of voltage and frequency. The operating voltage and frequency range of the PCU shall be sufficient enough to accommodate the allowable grid voltage and frequency variations.

PCU/ inverter shall be capable of complete automatic operation including wake- up, synchronization & shutdown.

It shall also have 150 percent overload capacity for 60 Sec.

It shall have LCD for displaying of all the operational and fault parameters, as detailed below:

    - AC output voltage, current, frequency and power factor.

    - DC input voltage, current (of each string) and DC power.

    - Fault logs/ data etc.

PCU shall have a communication interface for integration of the same to SCADA  and its monitoring.

Grid-tied Inverters shall bear the BIS mark as notified by the Ministry of New and Renewable Energy (MNRE), Government of India.

# Protection Features:

The Unit shall include appropriate self-protective and self-diagnostic feature to safeguard itself and the PV side from damage in the event of any of its component failure or from parameters beyond its safe operating range due to internal or external causes.

The unit shall have the following features for preventing inverter damage, other equipment damage, and personal injury hazards.

- DC and AC Type 2 SPD

- DC reverse polarity

- Anti-islanding: in conformity to IEEE 1547/ UL 1741/ IEC 62116

- Over temperature

- Ground insulation resistance detection

- O/C and S/C Protection

- PV string current monitoring

In addition to the above, Unit shall have following Grid Support Functions.

Active power regulation

The PCU shall be able to limit the active power exported to the grid based on the set point given from PCU. The PCU shall also be able to automatically limit the active power after an increase in grid frequency above a pre-set value. The ramp rate shall be adjustable during operation and start-up after fault. The requirement shall be as per CEA/ DERC regulations.

Voltage Ride Through & Frequency Ride Through

The PCU shall remain connected to the grid during a temporary dip or rise in grid voltage and frequency as per the LVRT and HVRT requirements of CEA Technical Standards for Connectivity to the Grid Regulations.

Tests:

Type Tests

The type test certificates as per the standards mentioned above should be from any of the ILAC/ IECEE member signatory accredited test centres. Laboratory accreditation certificate in this regard shall be submitted.

The contractor will have to substantiate the compliance of CEA Regulations using these test reports.

Routine Tests

Routine tests and acceptance tests shall be as per approved MQAP, as specified  in the SCC.

Installation:

String inverter shall be placed inside a canopy with a minimum of 150 mm in all directions or it can be installed on the column post of the Module Mounting Structure, below the modules, where such a canopy arrangement is not required.

# ACDB:

AC Distribution board shall be totally enclosed type, dust and vermin proof, suitable operation on 415V, 3 Phase, 4 wire, 50Hz, AC supply system, outdoor installation and shall be fabricated from CRCA sheet having a thickness not less than 2mm.

The DB shall confirm to IP-55 for ingress protection.

ACDB shall have all the indication bulbs to indicate on/ off/ trip status of the protective gear and the indication of all the three phases and line voltages (through phase indication bulbs and voltmeter) and the currents. Also, shall have MFM meter with RS 485 port.

MCCB(s) shall have thermal magnetic-based release with O/C & S/C and E/F protections.

The short circuit breaking capacity of the MCCBs shall not be less than 35kA (Ics=100%Icu).

Sheet steel work used in the construction of the ACDB shall be pre-treated with 7-tank chemical process before applying the two coats of zinc chromate primer followed by synthetic enamel/ epoxy paint of RAL-7032, matt finish powder coated. Paint thickness shall not be less than 50 micron.

All the protective switchgears and components in power/ control/ metering circuit should confirm to relevant IS/ IEC standards.

Main LT panel at Utility Block (back side of this building) having two feeders dedicated for solar PV system, so subsequently all ACDB & solar panel are going to connect these available feeders at Main LT Panel. Accordingly, distribution to be carried out for Solar PV System.

# Earthing:

The Earthing shall be provided in accordance with IS:3043-2018 “Code of practice for earthing.

The earthing conductor should be rated for 1.56 times the maximum short circuit current of the PV array.

All PV Modules, Structures, string inverter etc. shall be earthed by two distinct connections, as detailed below:

Each PV Module frame shall be earthed using copper wire having cross section of not less than 6 sq.mm. Star-type washers should be used when bolting the lugs of earthing cable.

Continuous copper earthing wire shall be run to connect a group of modules and both ends of the loop shall be bolted to the DC earth grid using bimetallic lugs and stainless-steel fasteners.

The connection between MMS and DC earth conductor shall be bolted.

PCU/ Inverter earthing: DC negative bus bar and PCU equipment earth shall be bonded to the PCU earth bus and connected to earth electrodes through flexible copper cable of sufficient cross section as recommended by the manufacturer. In case DC negative grounding is not possible, an appropriate anti-PID device shall be provided.

Cable trays shall be connected to the earth grid at minimum two places using galvanized steel flat.

Minimum size of the earth strip shall not be less than 25x3 mm.

There shall be four numbers separate earth pits i.e. 2 for AC ckt and 2 for DC ckt.

The earth electrode for pits shall be of copper bonded earth rods with thickness  of the copper coating not less than 250 micron. Suitable earth enhancing material shall be filled used to lower the resistance. Inspection chamber and lid shall be provided as per IS 3043.

# Lightning Protection System:

Since the building truss on which SPV to be installed has already the provision of lightning protection system and the system is to be installed and commissioned by the Main contractor of the building. This system will protect against the adverse effects of lightning strikes and    field thereof. So, Installation does not require any other Lightning protection system, only coordination and connecting to the building LPS system required.

# Cables:

For the DC cabling, 1.5 kV grade XLPO insulated and sheathed, UV stabilized annealed tinned plated copper conductor cables, conforming to IS 50618 shall be used. DC cable with positive polarity should have marking of red line on black outer sheath. These cables should have excellent resistance against heat, cold, water, oil, acids, alkaline & abrasion and will be black colour.

Cable on AC side will be of 1.1 kV grade, Aluminium conductor XPLE insulated FRLS cable PVC inner sheathed, extruded FRLS PVC ST2 outer sheathed, armoured cable conforming to IS: 7098-1.

Cables shall be sized based on the following factors:

- Rated current of module.

- The total voltage drop of the solar PV modules to the inverter shall not exceed 2 percent.

- Short circuit with stand.

- De-rating factors according to laying pattern.

Type test certificate from a NABL lab should be furnished during the approval of technical particulars of the cables.

# Cable laying:

Cable laying, termination, testing & commissioning shall be in accordance with IS 1255.

Solar cables shall be provided with UV-resistant printed ferrules and DC cables shall be provided with punched/ embossed aluminium tags. There should not be any cable joints in the solar cable.

Cable terminations shall be done with properly crimped lugs and suitable cable glands at the entry & exit point of the panels/ junction boxes/ cabinets. Bimetallic lugs shall be used for connecting Cu bus bar and Al cables or vice-versa.

Solar cables, wherever exposed to direct sunlight, shall be laid through DWC HDPE pipes.

Solar cables shall be tied to Module Mounting Structure using UV-resistant cable- ties.

# Cable Trays:

Cable trays and its fittings shall be factory fabricated and shall be made from rolled MS sheets having galvanization not less than 80 micron.

Thickness of sheet steel of cable trays, its fittings and coupler plate shall be min.  2mm.

# Data Acquisition system and performance monitoring:

There shall be SCADA system to be provided in the central command & control center, located in upper basement for performance monitoring and reporting of this SPV plant. The system should meet IS/ IEC 61724 standard. Typically, it consists of the following:

a) Hardware, licensed Software, Panels, Power Supply, HMI, Laser colour Printer, Gateway, Networking equipment and associated Cables, firewall, furniture for placement of the computer and printer etc.

b) Data acquisition system for capturing parameters from weather monitoring station and from string inverters i.e. all AC & DC electrical parameters such as I, V, CosΦ, three energy parameters – cumulative & instant etc. and also from the meters mounted on ACDB/ LT Panel on which integration has been done. String level monitoring is to be provided and reported in the SCADA so as to track individual strings.

There will be a workstation which acts as both an Engineering workstation (EWS) and an operating workstation (OWS) that display the parameters captured by data acquisition system in graphical form. The workstation will have latest windows operating system, i7 processor of latest generation, 1 TB HDD, 512 GB SDD, 8 GB RAM, built-in wifi/ LAN port and 25” LED monitor. Enterprise grade Licensed software should be provided, not a subscription based.

Apart from this, there will be a capacitive touchscreen display having size not less than 43” in the control room for extending the interface of workstation.

SCADA System shall have the provision to perform the following features and/or functions:

- Web-based Operator Dashboards: Showing key information on Generation, Performance and Current Status of various equipment in SLD form with the capability to monitor PV string parameters.

- Real-time Data Logging with Integrated Analytics & Reporting: Logging of all parameters – AC & DC side parameters as detailed in sub-clause 8(b) above parameters	from	weather	monitoring	station,	system	running	hours, Equipment Status and Alarms as well as derived/ calculated/ integrated values and as detailed aforementioned. The User interface shall be customizable and enable Report Generation and Graphical Analysis.

- Fault and System Diagnostics with time-stamped event logging.

- Integration with Automatic Solar Module Cleaning System and rest of the       system for efficient Plant Operations during O&M.

- Generate, store and retrieve user-configurable sequence of event reports.

- Transfer of plant data reliably, to Existing IBMS through API or any other means.

- The SCADA System shall be built over IoT-based architecture with       integrated Analytics, secure web access, enterprise software and Database.

The internet connectivity of the SCADA system will be through 5G data card and contractor will provide the same of adequate data capacity and speed during the entire contract duration including O&M.

Any charges towards cloud server hosting and domains registration/ renewal if any, for web-based SCADA system shall be in the contractor’s scope during the entire contract duration including O&M.

# Weather Monitoring System

The Contractor shall provide a) Pyranometer b) Temperature Sensors c) Anemometer with required software and hardware for the integration with SCADA, as per specification detailed below:

Pyranometer

The Contractor shall provide Class-A pyranometers (ISO 9060) of the specifications as detailed below along with necessary accessories for measuring incidental solar radiation at horizontal and inclined plane of array.

| Parameter | Specification |
| --- | --- |
| Spectral Response (50% points) | 0.31 to 2.8 micron |
| Operating temperature range | 0°C to +80°C |
| Ingress Protection | IP 67 |
| Resolution | Minimum +/- 1W/m2 |
| Output | 4–20 mA/RS485 |

Calibration certificate with calibration traceability to World Radiation Reference (WRR) or World Radiation Centre (WRC) shall be furnished in this regard.

Temperature Sensor

The Contractor shall provide minimum three numbers temperature sensors (1 (one) for ambient temperature measurement with shielding case and 2 (two) for module temperature measurement). The temperature sensor shall be RTD/ Semiconductor type with a range of 0°C to 80°C.

Anemometer: 1 number ultrasonic wind sensor for measurement & detection of wind speed and direction.

| Parameter | Specification |
| --- | --- |
| Velocity range with accuracy limit | 0-60m/s with +/-2% accuracy @12 m/s; Resolution: 0.01m/s |
| Wind direction range with accuracy limit | 0 to 360°C (No dead band) with +/-2°C accuracy@12m/s; Resolution: 1°C |
| Mounting Bracket | Anodized Aluminium bracket, SS mounting bolts |
| Protection Class | IP 66 |
| Output | RS 485 |

# Automatic Solar panels cleaning system:

There shall be automatic solar panels cleaning system to clean the solar panels from dust which consists of the required nos. of water spray nozzles on every solar module, PVC piping for supplying of pressurized water to these nozzles through a pump, and a controller for automatic and time-based operation.

The water supply for this cleaning system can be tapped at one point from the terrace-mounted domestic water SMC panel tanks.

BOQ-SOLAR PV WORKS

| SL. NO. | ITEM DESCRIPTIONS | UNIT | QTY. | RATE (Rs.) | AMOUNT (Rs.) |
| --- | --- | --- | --- | --- | --- |
|  | SOLAR PV WORKS |  |  |  |  |
| 1.0 | Design, Supply, Installation at various locations as per site, Testing and Commissioning of on grid Solar Photo Voltaic Power Plant conforming to MNRE specifications as amended and Tender Specifications, consisting of Mono Crystalline silicon solar cells, net metering facility, along with string inverter, cables, cable tray, ACDB and DC DB with necessary protections, earthing, mounted on Aluminium/ GI structure of suitable strength with following components complete as required:- |  |  |  |  |
| i) | Solar Photovoltaic Module of minimum capacity 540Wp, manufactured in India, conforming to IEC 61215, IEC 61730-Part-1, IEC 61730-Part-2 amendment up to date. Efficiency Solar Photovoltaic Module shall be guaranteed to 90% for upto 12 years and 80% from 12 to 25 years. |  |  |  |  |
| ii) | Complete with reverse power protection devices, AC surge protection devices. |  |  |  |  |
| iii) | Solar power shall be evacuted into Main LT panel at Utility Block, Substation at 415Volts. ESE Lightning Protection system has to be provided in accordance with IS/ IEC 62305. |  |  |  |  |
| iv) | Power Evacuation permission from local DISCOM including Load Flow Study, NOC, and Permission for connection to GRID, SLD approval from DISCOM, if required & Approval for Grid Synchronization. |  |  |  |  |
| v) | All materials used must have a proven history of reliable and stable operation in external outdoor applications. Solar modules are designed to operate and perform in relative humidity up to 100% with temperatures between -10 Deg C and +85 Deg C and with stand gust up to 150km/h from back side of the panel. |  |  |  |  |
|  | Considering the above details and tender specifications, installations are as below, |  |  |  |  |
| a) | Complete system as specified above (As per tender specifications and with structure less than 1 mtr. height supports ). | kWP | 307.2 |  | - |
| b) | Complete system as specified above (As per tender specifications and with structure tentative 4.65 mtr. height supports or as per drawings). | kWP | 174.4 |  | - |
| SL. NO. | ITEM DESCRIPTIONS | UNIT | QTY. | RATE (Rs.) | AMOUNT (Rs.) |
| c) | Complete system as specified above (As per tender specifications and with structure tentative 9.17 mtr. height supports or as per drawings). | kWP | 92.34 |  | - |
|  | Note: MS Structure minimum size 105Tonne may require, but structural design will be part of successful bidder's scope of work. |  |  |  |  |
|  | TOTAL CARRIED OVER TO SUMMARY |  |  |  | - |

LIST OF APPROVED MAKES

Instruction to bidders:

- Submit catalogues with the offers.

- Produce test certificates for equipment/ material supplied with bills for certification.

- Submittals and samples must be gotten approved before supply, from Owner/ Project Managers/ Architect/ Consultants.

|  | Solar PV System |  |  |  |
| --- | --- | --- | --- | --- |
| 1. | Dual Glass PV Solar module |  | a | Adani |
|  | (high efficiency >19.75%) |  | b | Benq |
|  |  |  | c | Emvee |
|  |  |  | d | Jakson |
|  |  |  | e | Renewsys |
|  |  |  | f | Tata Solar |
|  |  |  | g | Vikram Solar |
|  |  |  | h | Waaree Energies |
|  |  |  | i | Panasonic |
| 2. | Grid Tied Solar Inverter |  | a | Delta/ Schneider/ Emerson/ SolarEdge |
| 3. | Solar PV Controller |  | a | Dief |
|  |  |  | b | Wood Word |
| 4. | LT/ DC Cable |  | a | Finolex |
|  |  |  | b | Havells |
|  |  |  | c | KEI |
|  |  |  | d | Polycab |
| 5. | LT/ MV cubical panel/ AMF/ APFC |  | a | Adlec |
|  | Panel/ Battery Charger |  | b | Ambit |
|  |  |  | c | Control & Switchgear |
|  |  |  | d | Sterling Generators |
|  |  |  | e | Tricolite |
| 6. | MCCB’s |  | a | Schneider: NSX Series |
|  |  |  | b | Siemens: 3VL Series |
|  |  |  | c | Mitsubishi: WS Series |
|  |  |  | d | Legrand: equivalent model |
|  |  |  | e | L&T: equivalent model |
|  |  |  | f | ABB: equivalent model |
| 7. | ACB’s |  | a | Schneider: NW Series |
|  |  |  | b | Siemens: 3WL Series |
|  |  |  | c | Mitsubishi: WS Series |
|  |  |  | d | Legrand: equivalent model |
|  |  |  | e | L&T: U-pact |
|  |  |  | f | ABB: equivalent model |
| 8. | MCB’s |  | a | Legrand |
|  |  |  | b | Siemens |
|  |  |  | c | Schneider |
|  |  |  | d | ABB |
|  |  |  | e | L&T |

In case any of makes for any of the material is missed out in the above list for using at site then the contractor shall inform the Project Manager-LNMIIT about the same and obtain the approval. Thereafter, he can proceed with the supply of the material.

Annexure-1

AFFIDAVIT

- I, the undersigned, do hereby certify that all the statements made in the required statements are true & correct.

- The undersigned also hereby certifies that neither our firms M/s___________________ have abandoned any work in previous projects or in any other Department nor any contract awarded to us for such works have been rescinded, during last five years prior to the date of this bid.

- The undersigned understand and agrees that further qualifying information may be requested and agrees to furnish any such information at the request of the LNMIIT, Jaipur.

………………………………………………………..

(Signed by an Authorized Person of Firm)

………………………………………………

(Title of the Authorized Person)

…………………………………………….

(Name of Firm )

On non-judicial stamp paper of minimum Rs. 100/-)

Form of Bank Guarantee for Earnest Money Deposit/                     Performance Guarantee/ Security Deposit

To

M/s LNM Institute of Information Technology,

Gram: Rupa ki Nangal,

Post: Sumel

Jaipur-302031

Rajasthan.

- In consideration of M/s LNMIIT – jointly established in 2002 by the state government of Rajasthan and the Lakshmi & Usha Mittal foundation, having its registered office at Gram: Rupa Ki Nangal, Post Sumel, Via Jamdoli, Jaipur, Rajasthan ( India ) – 302031  (hereinafter called “the Company” (which expression shall include its successor in business and assignees) have agreed to accept irrevocable bank guarantee of Rs……………………….( rupees………………….only ) valid upto……… (date) as Earnest Money Deposit from…………………( name and address of the “contractor”) for compliance of his obligations in accordance with the terms and conditions of the said NIT.

OR

In consideration of M/s LNMIIT – jointly established in 2002 by the state government of Rajasthan and the Lakshmi & Usha Mittal foundation, having its registered office at Gram: Rupa Ki Nangal, Post Sumel, Via Jamdoli, Jaipur, Rajasthan ( India ) – 302031 (hereinafter called “the Company” (which expression shall include its successor in business and assignees) have agreed to accept irrevocable bank guarantee of Rs……………………….( rupees………………….only ) valid upto……… (date) as Performance Guarantee/ Security Deposit/ Mobilisation Advance from the said contractor for compliance of his obligations in accordance with the terms and conditions of the agreement.

- We, ................ (Indicate the name of the bank) ..........................., (herein after referred to as “the Bank”), hereby undertake to pay to the COMPANY an amount not exceeding Rs ................................ (Rupees.............................................. only) on demand by the COMPANY within 10 days of the demand.

- We, ......................... (Indicate the name of the Bank) ................, do here by undertake to pay the amount due and payable under this guarantee without any demur, merely on a demand from the Government stating that the amount claimed is required to meet the recoveries due or likely to be due from the said Contractor. Any such demand made on the Bank shall be conclusive as regards the amount due and payable by the Bank under this Guarantee. However, our liability under this guarantee shall be restricted to an amount not exceeding Rs................... (Rupees ........................ only)

- We, .......................................(indicate the name of the Bank) ..................., further undertake to pay the Company any money so demanded notwithstanding any dispute or disputes raised by the contractor in any suit or proceeding pending before any Court or Tribunal, our liability under this Bank Guarantee being absolute and unequivocal. The payment so made by us under this Bank Guarantee shall be a valid discharge of our liability for payment there under and the Contractor shall have no claim against us for making such payment.

- We, ....................................(indicate the name of the Bank..............................., further agree that the Company shall have the fullest liberty without our consent and without affecting in any manner our obligation here under to vary any of the terms and conditions of the said agreement or to extend time of performance by the said Contractor from time to time or to postpone for any time or from time to time any of the powers exercisable by the Company against the said contractor and to forbear or enforce any of the terms and conditions relating to the said agreement and we shall not be relieved from our liability by reason of any such variation or extension being granted to the said Contractor or for any forbearance, act of omission on the part of the Company or any indulgence by the Company to the said Contractor or by any such matter or thing whatsoever which under the law relating to sureties would, but for this provision, have effect of so relieving us.

- We, ...................(indicate the name of the Bank) ........................................................ further agree that the Company at its option shall be entitled to enforce this guarantee against the Bank as a principal debtor at the first instance without proceeding against the Contractor and notwithstanding any security or other guarantee the Company may have in relation to the Contractor's liabilities.

- This guarantee will not be discharged due to the change in the constitution of the Bank or the Contractor.

- We, .......................................(Indicate the name of the Bank) ...................undertake not to revoke this guarantee except with the consent of the Company in writing.

- This Bank Guarantee shall be valid up to ...................................................... unless extended on demand by the Government. Notwithstanding anything mentioned above, our liability against this guarantee is restricted to Rs......................... (Rupees............................................................only) and unless a claim in writing is lodged with us within the date of expiry or extended date of expiry of this guarantee, all our liabilities under this guarantee shall stand discharged.

Date :…………….

Witnesses:

- Signature……….

Name and Address							Authorised signatory

Name ……….

Designation……..

Staff code No…….

Bank seal………..

- Signature……….

Name and Address

- Date to be worked out on the basis of validity period of 90 days where only financial bids are invited and 180 days for two/three bid system from the date of submission of tender.

- In paragraph 1, strike out the portion not applicable. Bank Guarantee will be made either for earnest money or for performance guarantee/security deposit/mobilization advance, as the case may be.

PRICE BID

(To be Paid separately)

Name of the Project: Construction of LNMIIT International Centre for Artificial intelligence (LICAI) (G+5) at Jaipur.

Sub Head: Solar PV Works.

| Sno. | Description | Amount |
| --- | --- | --- |
| 1.0 | Solar PV Works |  |
| 1.1 | Item as described in serial no. 1.1 of the schedule of quantities |  |
| 1.2 | Item as described in serial no. 1.2 of the schedule of quantities |  |
| 2. | Comprehensive Maintenance for a period of next five years (05) after the completion of Defects Liability period of one year for serial no. 1 (1.1+1.2) |  |
|  | Total in Figures |  |
|  | In Words: |  |