Tender No:. 2025-26/Estate/2B/LNM-1240

The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System”. Bidders can submit their sealed offers/s at the following address by Email/Speed-Post/ Registered Post/ By-hand/courier before 05:00 PM on 14.03.2026 (Last date of bid receiving).

Filing of Tender:

Option 1: Physical submission of offers (hard copy) in sealed envelopes.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the institute in person/ Speed-Post/ Registered Post/ By-hand/courier of the Institute after marking due entries in the Receipt Book available with the Security Officer at the main gate.

The tender subject and reference number must be mentioned on the envelope.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Option 2: Password-protected online submission via Email

Password-protected offers can be submitted by the bidders via email at the below-mentioned email IDs.

tender-document@lnmiit.ac.in (password-protected document)

tender-password@lnmiit.ac.in (password only)

The tender subject and reference number must be mentioned in the subject line of the emails.

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory, are required to be submitted in two separate envelopes/emails.

Envelopes/Emails should be duly marked as follows:

- Technical bid for the “supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System”. (Technical bid must be submitted without password protection)

- Commercial Bid for the “supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System”. (The Commercial bid must be submitted with password protection.)

Both Envelopes/files should be enclosed/attached in a single envelope/email bearing the heading “Bid for the “supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System (Tender No. : 2025-26/Estate/2B/LNM-1240) ”.

Note: The bidders/vendors are requested to go through the tender document carefully and ensure compliance with all specifications/instructions in this tender

Bids are liable to be rejected:

- If the above-mentioned bid submission procedure is not followed.

- Incomplete and non-conforming bids.

- Arbitration: All disputes and differences arising between the two parties in connection with this order shall be mutually settled as far as possible, failing which, all such disputes shall be referred to arbitration and settlement under the provision of the Arbitration and Conciliation Act, 1996 and as amended from time to time or any such law for the time being prevailing in India. The venue of such arbitration shall be Jaipur.

Technical Bid: (in a separate sealed envelope/via email) without password

# Bid for supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricated Stand

# (Tender No. : 2025-26/Estate/2B/LNM-1240)

Bidder is required to furnish the requisite details as per the below mentioned table format and proof of such documents to be uploaded along with the bid under respective title/ headings as mentioned at column no ‘C’ accordingly.

| S.No. | Title/ Heading Details sought by buyer | Details/ Certificate No. (Attached Y/N) |
| --- | --- | --- |
| A | B | C |
| 1. | Bidder Firm Name & Registration No, |  |
| 2. | Bidder’s Company profile or brief note |  |
| 3. | PAN Card No,. |  |
| 4. | GST Number |  |
| 5. | List of Directors/ Partners/Proprietor/ Members of the Bidder’s Firm |  |
| 6. | Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members |  |
| 7. | Bidder Turnover - Average annual turnover for last three years |  |
| 8. | The Client List with some purchase orders and satisfactory certificate (to whom the vendor has delivered the goods/provided the services in the past (Three (03) purchase orders/work orders, at least one from each of the last three years, including the previous year.) |  |
| 9. | If the bidder is authorized by the OEM/Manufacturer. Proof of the same is to be submitted with the Technical Bid |  |
| 10. | An undertaking (self-certificate) that the agency has not been blacklisted by a Central/State/UT Government Institutions and there has been no litigation with any government department/institution on account of any services/supplies. |  |
| 11. | Scanned copy of EMD/ Tender Fees paid through RTGS/NEFT (if required/asked in the tender) |  |
| 12 | Xerox copies of MoUs with previous colleges (minimum three) must be attached. (Applicable for student fest only). |  |

## Scope of work

- The scope of work will cover the supply/service/SITC of given  items at LNMIIT Jaipur campus.

- The Vendor is required to submit the complete documentation of the supplied item after delivery.

- SITE CONDITION:

Before quoting, the contractor must visit the site to inspect the work and shall fully acquaint himself about the conditions and scope of work with regards to accessibility of site required for the satisfactory execution of work. No compensation on account of any site difficulties will be entertained at a later date, after the award of the works.

Technical specification:

| S/No | Specification | Parameter requirements |
| --- | --- | --- |
|  | Make | Numeric |
|  | Model | Numeric Onfiniti |
| 1. | UPS Capacity | 10 kVA |
| 2. | Technology | a. True online double conversion b. IGBT based rectifier & inverter c. Inbuilt PRS kit for Parallel Option in future |
| 3. | Input Parameters: |  |
| a. | Voltage | 230 VAC, 1 Phase |
| b. | Voltage Range | 110V to 300 VAC based on load level |
| c. | Frequency | 50 Hz |
| d. | Power Factor at rated load | Unity at full load |
| e. | Current Harmonic Distortion | Less than 10% |
| 4. | Output Parameters: |  |
| a. | Voltage | 220/230/240 VAC +/ - 1%, 1 Phase |
| b. | Frequency | 50 Hz +/- 0.25 Hz (in Battery Mode) +/- 6% (in Sync) |
| c. | THD v | < 2 % for Linear Load ; < 5 % for Non Linear Load |
| d. | Overload rating | 105 to 109 % - 10 min ; 110 to 129 % - 60 sec ; 150 % - 10 seconds |
| e. | Output waveform | Pure sinewave |
| f. | Crest Factor | 3 : 1 |
| g. | Output Power Factor | 0.9 |
| h. | Over all Efficiency | >93% without Transformer |
| 5. | Battery Parameters: |  |
| a. | Batteries Type ( 12V VRLA) | Sealed Maintenance Free Batteries ( Exide ) |
| e. | Backup Time | 30 Mins. |
| f. | DC Voltage | 192 VDC |
| h. | Battery Rack | Battery Rack / Stand |
| i. | Transfer time | UPS to Battery Mode : 0 ms |
| j | Three Stage Charger | Constant Voltage / Constant Current / Float Charging with Temperature Compensated Charger |
| k | Charging Capacity | 10 % of the Battery AH Capacity |
| 6. | Bypass: |  |
|  | Static Bypass | Required (Inbuilt) |
|  | Transfer time | < 4 ms in Sync Mode |
|  | Bypass parameter configurable via front panel | Required |
|  | Manual Bypass | Required (Inbuilt) |
| 7. | LCD Display / Alarm / Protection |  |
| a. | Metering Data |  |
|  |  | Input Voltage |
|  |  | Input Frequency |
|  |  | Output Voltage |
|  |  | Output Frequency |
|  |  | Output Power in Watts |
|  |  | Output Current |
|  |  | Load Level in % |
|  |  | Battery Voltage |
|  |  | Battery Level |
|  |  | Temperature |
|  |  | Event Log |
|  |  | Battery Test |
| b. | Status Information Data |  |
|  |  | Normal |
|  |  | Bypass |
|  |  | Battery |
|  |  | Fault |
|  |  | Converter Mode |
|  |  | Eco Mode |
|  |  | Bypass Mode |
|  |  | Battery Mode |
| c. | Fault / Waring Indication |  |
|  |  | Over Load |
|  |  | Charger Fail |
|  |  | Inverter Fault |
|  |  | Over Temperature |
|  |  | Short Circuit |
|  |  | DC low / High |
|  |  | Output Low / High |
|  |  | Fan Fail |
|  |  | Battery Disconnected |
| d. | Protection Required | Input High / Low |
|  |  | Over Load |
|  |  | Short Circuit |
|  |  | Over Temperature |
|  |  | Battery Over Charge |
|  |  | Battery Deep Discharge |
| e. | Audible Alarm | Battery Mode |
|  |  | Low Battery |
|  |  | Fault |
|  |  | Over Load |
|  |  | Bypass Mode |
| 8. | Other Features: |  |
| a. | Communication Port | RS 232 & USB |
| b. | Cold Start | Required |
| c. | Auto Restart | Required |
| d. | EPO | Required |
| e. | Generator Compatibility | Required |
| f. | SNMP Card | Optional |
| g. | Operating Temperature | 0 to 45 Deg C without derating |
| h. | Storage Temperature | 0 to 60 Deg C |
| i. | Humidity | upto 95 % |
| j. | Altitude | < 1000 meters |
| 9. | Connection |  |
|  | Input | Terminal Block |
|  | Output | Terminal Block |
|  | Battery | Terminal Block |
| 10. | Credential / Reports |  |
|  | ISO 9001 2015 | Copies Required |
|  | ISO 14001 2004 | Copies Required |
|  | ISO 45001: 2018 | Copies Required |
|  | BIS Certificate | Copies Required |
|  | JIS 8702C for battery | Copies Required |
|  | Manufacturing facility | a. Make in India. b. OEM Minimum 10 Years presence in India. |
|  | Service facility | UPS manufactures should have not less than 200 service centers accross India. |
|  | Turn Over | Vendor should have turn over more than 300 crores |
| 11. | Warranty /After Sales Support |  |
|  | Service Support | Directly from OEM for UPS & Batteries Both |
|  | Warranty | Onsite 24 Months on UPS & Batteries |
|  | Numeric Authorized service center | Local Authorized service center in Jaipur |
|  | Authorized Supplier Certificate | Numeric |

Commercial Bid: (in separate sealed envelope/password protected file in Email) with password protection

Bid for Supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System

(Tender No. : 2025-26/Estate/2B/LNM-1240)

| S. No. | Particulars | Make | Qty. | UOM | Rate | Amount |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Supply, Instruction, testing and commissioning of 10 KVA Single Phase online UPS System with two-year warranty | Numeric/APC/Socomec | 3 | Nos. |  |  |
|  | Total |  |  |  |  |  |
|  | GST_______ |  |  |  |  |  |
| TOTAL (including taxes) |  |  |  |  |  |  |

GENERAL TERMS AND CONDITIONS:

- All applicable taxes such as GST must be clearly mentioned. If not specified, it shall be deemed that all such charges are included in the quoted price.

- If the supplier does not have a particular item or proposes a different make than that specified in the tender, the same must be clearly highlighted in the bid.

- Prices must be inclusive of all charges such as packing, forwarding, transit insurance, transportation, loading, unloading (up to 50 meters), installation, and any other incidental expenses.

- Bid must be submitted on an F.O.R. basis for delivery at: The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur – 302031.

- Bid shall remain valid for a minimum period of 30 days. No change in prices will be accepted during the validity period.

- The LNMIIT reserves the right to reject any quotation without assigning any reason.

- Payment terms shall be mutually decided and agreed upon between the Institute and the vendor.

- The bidder must submit a No Conflict of Interest Declaration along with the bid.

- The bid must be submitted on the company’s letterhead and in the LNMIIT-prescribed format only.

- Any item or service not being supplied by the bidder must be clearly mentioned separately in the bid.

- Vendors must provide a photocopy of their cheque/cancelled cheque along with the invoice for payment processing.

- Prices shall be quoted in Indian Rupees (INR) only.

- Total prices shall be quoted for the complete scope of work as per technical specifications, inclusive of all taxes, duties, insurance, packing, forwarding, and incidental charges.

- Agencies or individuals who are debarred or blacklisted are not permitted to participate in the tendering process. Any agency engaging a debarred person for negotiations or representation is also liable to be debarred.

- If the work is not completed within the stipulated time mentioned in the work order, the competent authority of LNMIIT reserves the right to accept partial work on suitable terms, cancel the supply/work order, withhold or stop payment, forfeit the Earnest Money Deposit, or debar the agency. The decision of the Competent Authority shall be final and binding.

- In case two or more bidders quote the same rates, the final selection shall be made through a draw of lots conducted by a committee comprising LNMIIT administrative members(PCC).

- Vendors are required to visit the site and conduct a detailed survey before submitting their bid to understand the exact requirements. No request for additional items or modifications will be entertained later.

- A pre-bid meeting and/or site visit may be arranged prior to submission of bids to clarify any doubts regarding project details, scope of work, and required documents.

Signature with seal