Supply, Installation, Testing and Commissioning of Upgradation Work from 11 kV to 33 kV for External Electrical HT Panels, Cabling and Transformer Work for JVVNL DS – HT Metering & Indoor Distribution 33 kV System at LNMIIT Substation

Tender No. 2025-26/Estate/2B/LNM-1339

TENDER DOCUMENT

FOR

Upgradation Work 11 kV to 33 kV Electrical Power Supply AT LNMIIT Substation

THE LNM INSTITUTE OF INFORMATION TECHNOLOGY,

RUPA KI NANGAL, VIA JAMDOLI, JAIPUR, RAJASTHAN.

Index

| Sno. | Description | Page No. |
| --- | --- | --- |
| 1. | Notice Inviting Tender | 3 |
| 2. | Instructions to bidders | 4 |
| 3. | Eligibility Criteria | 6 |
| 4. | Scope of work | 7 |
| 5. | General Terms of Conditions | 9 |
| 7. | Technical Specifications | 11 |
| 8. | List of Approved makes | 25 |
| 9. | Schedule of Quantities | 27 |
| 10. | Affidavit | 35 |
| 11. | Proforma EMD/Performance bank guarantee/Security deposit | 36 |
| 12. | Price bid | 39 |

Notice Inviting Bid

(Competitive bidding)

The Director on behalf of THE LNM INSTITUTE OF INFORMATION TECHNOLOGY, JAIPUR (“LNMIIT”) having its office at Rupa ki Nangal, Via Jamdoli, Jaipur  invites item-rate tenders from eligible firms/agencies for the following works through hard-copy submission under a two-bid system: the Technical Bid and the Financial Bid both has to be submitted in hard copy only.

Name of the Project: Supply, Installation, Testing and Commissioning of Upgradation Work from 11 kV to 33 kV for External Electrical HT Panels, Cabling and Transformer Work for JVVNL DS – HT Metering & Indoor Distribution 33 kV System”.  at LNMIIT Jaipur.

Sub Head: Supply Installation, Testing and commissioning of Upgradation Work 11 kV to 33 kV works.

Detail of the Tender bid:

Earnest Money: Rs.9,00000.00

Period of Completion: BY 30 June 2026.

Mobilization time - Nil

Date of Issue of Bid: 28.03.2026

Date & Time of Pre-Bid Meeting: 1100hrs 01.04.2026

Last date & time of submission of bid document: 08.04.2026 by 05.00 PM.

Director

LNMIIT

Instructions for the Bidder

- This Notice Inviting Tenders (Part-1,2,3 & 4) i.e. Eligibility criteria for the bidder, Scope of work, Terms & conditions, Comprehensive warranty, Defects liability period, Comprehensive Maintenance for 5 years, General terms & conditions, General technical conditions, technical specifications, List of approved makes, Affidavit, Proforma for Bank guarantee, Price bid  shall form the TENDER DOCUMENTS.

- Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the institute in person/ Speed-Post/ Registered Post/ By-hand/courier of the Institute after marking due entries in the Receipt Book available with the Security Officer at the main gate.

The tender subject and reference number must be mentioned on the envelope.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

The bid document shall be submitted in two envelopes consisting of the following:

Envelope 1: Bid document duly signed and stamped by the authorised signatory along with the EMD as specified.

Envelope :2: Price Bid.

Price bid envelope i.e envelope 2 will be opened only of those bidders who successfully meet the eligibility criteria.

- The Contractors are to pay the amount of earnest money as specified in the tender notice separately along with the Tender. Tenders for which earnest money deposit has not been received separately shall be returned unopened/not to be considered for further processing.

- The Contractor should certify that he has studied the work at site and acquainted himself with the position regarding, materials & labour required for the work.

- Should the Contractor notice any discrepancy or error in any statement made, he shall immediately bring to the notice of the LNMIIT-Electrical Engineer of LNMIIT, Jaipur (jrengineer.electrical1@lnmiit.ac.in) and obtain clarifications before submitting the tender.  The tender shall be recorded as such in the covering letter to the tender, failing which the Owner shall have right to ask the Contractor to execute the Work according to the statement made in the tender, without any compensation.

- The Rates should be quoted in figures and words, and the respective amounts or total shall be given by each TENDERER. In case of any difference in rates in figures / words, those given in words, shall hold good as quoted rate and in case of any difference in rates and Total amount, quoted Rates shall hold good.

- The TENDERS shall remain valid for acceptance for 60 days from the last date of Submission.

- The successful TENDERER shall be intimated about the Award of work, and the Earnest Money Deposits of other TENDERERS shall be returned without any interest on the amount deposited.

- The LNMIIT reserves the right to reject any / all TENDERS without assigning any reason and shall not be bound to accept the lowest or any other TENDER.

- TENDER not accompanied by the requisite EARNEST MONEY DEPOSIT in the specified form or accompanied with the conditional offer are liable to be summarily rejected.

- The Bidder should stamp and sign the document in order to ascertain that he complies with all the specifications and terms and conditions mentioned in the Bid.

- Earnest money deposit will be paid online or thru Demand draft or by online bank transfer to the following bank account:

Account Name   	:	“The LNM Institute of Information Technology”

Account No.    	:       001201038168

Bank                    	:       ICICI Bank Ltd.

Branch         	:     C-Scheme, Jaipur

IFSC Code     	:       ICIC0000012

Account type    	:       Saving account

The acknowledgement of the EMD should be mailed to the finance officer on the email: cfo@lnmiit.ac.in and purchase officer on the email: purchase.officer@lnmiit.ac.in.

- Co-ordination with other agencies / contractors appointed directly by the owner:

The Successful bidder shall co-ordinate and provide facilities for the contractors appointed by the LNMIIT.

In addition to the above Clauses all requirements will have to be implemented by the Bidder for all persons employed by him working on the Site including monitoring to ensure implementation etc., employed directly by the Owner.

- The tender of any Contractor not complying with any of the above instructions 1 to 12 may be rejected.

I / We have carefully read the above said instructions have understood the same and shall comply with the same.

Place : 						Signature of the Contractor

Date:							With seal & address

Name of the Contractor: -

Contact No.

e-mail id:

Part-1

Eligibility Criteria for 11 Kv to 33 KV Upgradation Work

| no. | Parameter | Documents to be submitted by Bidder |
| --- | --- | --- |
| 1 | Earnest Money Deposit: | The bidder should submit and EMD of Rs. 9,00,000/- (Nine lacs only) |
| 3. | Bidder Turnover | The OEM should submit the CA Certified turnover document for the Financial Turnover of Bidder for last three Financial Years i.e. FY 2022-23, 2023-24, and 2024-25 . |
| 4. | Bidder Authorized Certificate | The bidder must fulfil the following: - Must have executed at least two (2) similar 33 kV or above level EPC projects in the last 5 years. - Must have valid A-Class Electrical Contractor License. - Must be registered vendor/contractor in JVVNL / RVPN / State DISCOM (preferred). - Average annual turnover of Rs. 5 crore in last 3 years. - Must submit GST, PAN, PF/ESI registration. |
| 5. | Experience criteria & Past performance for the OEM | To qualify, each bidder should have supplied /executed similar category product/work i.e SITC of any Govt. Department/PSU/ Public Listed Company in last five years with: - Average annual turnover of Rs. 5 crore in last 3 years. Requirements: - Completion certificates mentioning order number and order value issued by the relevant competent Authority |
| 8. | GST number | The bidder should attach GST number detail mandatorily |
| 9. | PAN Card | The bidder should attach PAN card detail mandatorily |
| 10. | BOQ Compliance | The Bidder should stamp and sign the document in order to ascertain that he complies all the specifications and terms and conditions mentioned in the Bid |
| 11. | Affidavit as per Annexure-1 | The Bidder should submit the Affidavit as per Annexure-1 |

Part-2

Scope of Work:

The contractor shall execute the work on an Item rate basis including:

2.1 Design & Engineering

- Detailed survey from LNMIIT Campus Gate No. 3 to 11 KV Substation point.

- Survey, approval of SLD, Preparation of route plan for 11KV and 33 kV line, including Under Ground cable

- Load calculation and preparation of single-line diagram (SLD). Basic SLD will be provided by LNMIIT.

- Obtaining all necessary approvals from JVVNL and Electrical Inspectorate or any other statutory authorities required.

2.2 Procurement & Supply

- As per BOQ

2.3 Execution / Construction

- As per BOQ

2.4 Approvals / Coordination

- submission of drawings to JVVNL.

- Getting line shutdowns.

- Testing and commissioning.

- Final charging approval from JVVNL & Electrical Inspector and any other authorities.

2.5 Handover

- As-built drawings

- Test reports

- Warranty certificates

- Training to LNMIIT technical team

2.6 COMPLIANCE WITH REGULATIONS AND INDIAN STANDARDS: All works shall be carried out in accordance with relevant regulation both statutory and those specified by the Indian Standards related to the works covered by this specification. In particular, the equipment and installation will comply with the following:

(i) Factories Act.

(ii) Indian Electricity Rules.

(iii) B.I.S. & other standards as applicable.

(iv) Workmen’s compensation Act.

(v) Statutory norms prescribed by local bodies like CEA, Power Supply Co. inspectorate, etc.

Part-3

Terms & Conditions for warranty/defects liability period of Five year

1) The Contractor shall repair or replace any parts detail in the following clause which are found to be defective.

2) The equipment covered in the contract for maintenance includes: -

a) Examine periodically all safety devices and governors and make all customary safety tests.

b) Systematically examine and adjust the following components: -

3) Any accident that occurred due to negligence will be the entire responsibility of the contractor.

4) The tenderer should in his own interest visit the site and get familiarized with the site conditions before tendering.

5) The work shall be carried out as per technical Specifications and schedule of quantities specified in this document the entire satisfaction of the Electrical Engineer.

6) The tendered rates shall be deemed to include all services covered under this contract and no extra payment will be made on this account.

8) Maintenance:

a. The comprehensive maintenance, routine as well as preventive maintenance for 05 years from the date of completion of DLP shall be carried out and the record of the same shall have to be maintained by OEM/Authorized service provider.

b. Sufficient trained and experienced staff & Engineer shall be made available to meet any exigency of work during the guarantee period of one year from the handing over of the installation.

c. The following activities are covered under the scope of work, including cost of spares, provision of repair component and replacement of items as required.

Part-4

General Terms & Conditions

1) The intending bidder must read the terms and conditions of the bid carefully. He should only submit his bid if he considers himself eligible and he is in possession of all the documents required.

2) Information and Instructions for bidders posted shall form part of bid document.

3) The LNMIIT-Jaipur reserves the right to reject any prospective bid at any point of time, if the documents provided by the bidder appear to be fake or any false information is provided by the bidder.

4) The intending contractor is advised to visit the site of work, of his own, to acquaint himself regarding site details etc. prior to quoting the tender.

5) Payment Terms:

Payment to the bidder shall be released as follows:

- Advance Payment:
10% of the quoted cost shall be paid as advance after award of work and submission of Performance Security/Advance BG.

- Delivery Stage:
50% of the quoted cost shall be paid after successful delivery of all materials/items at site.

- Installation, Testing & Commissioning Stage:
35% of the quoted cost shall be paid after successful installation, testing, and commissioning of items covered under Serial No. 1 to 3.

- DLP Completion Stage:
The remaining 5% of the quoted cost for Serial No. 1 to 3 shall be released after successful completion of the Defect Liability Period (DLP).

7) Intending bidders are advised to inspect and examine the site and its surroundings and satisfy themselves before submitting their bids as to the nature of the ground  the form and nature of the site, the means of access to the site, the accommodation they may require and in general shall themselves obtain all necessary information as to risks, contingencies and other circumstances which may influence or affect their bid. The bidder shall be deemed to have full knowledge of the site whether he inspects it or not and no extra charge consequent on any misunderstanding or otherwise shall be allowed. The bidders shall be responsible for arranging and maintaining at his own cost all.

8) It is required that each Bidder/Contractor (including their respective officers, employees and agents) adhere to the highest ethical standards, and report to the Director-LNMIIT all suspected acts of fraud or corruption or Coercion or Collusion of which it has knowledge or becomes aware, during the tendering process and throughout the negotiation or award of a contract.

9) This guarantee shall be in the form of Insurance Surety Bonds, Account Payee Demand Draft, Fixed Deposit Receipt or Bank Guarantee from any of the Commercial banks in accordance with the prescribed form as provided in the bid. In case, the Bidder fails to deposit the said Performance Guarantee within the period as mentioned above including the extended period, if any, the Earnest Money deposited by the Bidder shall be forfeited automatically without any notice to the Bidder. The earnest money deposited along with the bid shall be returned after receiving the aforesaid performance guarantee.

10) Rates: The rates quoted by the tenderer shall be firm and inclusive of all taxes (including works GST, labour cess), duties, levies, octroi etc. and all charges for packing forwarding, insurance, freight and delivery, installation, testing, commissioning etc. and clearance required if any.

11) The Contractor has to carry out comprehensive, routine and preventive maintenance as per manufacturer’s standard for a period of minimum 12 months from the date of handing over. Nothing extra shall be paid on this account.

12) WARANTEE: All equipment’s shall be guaranteed for a minimum period of 12 months, from the date of taking over the installation by the department/Client against unsatisfactory performance and/or breakdown due to defective design, workmanship or material. The equipment or components, or any part thereof, found defective during the guarantee period shall be forthwith repaired or replaced free of cost, to the satisfaction of the Electrical Engineer. In case it is felt by the department that undue delays are being caused by the contractor in doing this, the same will be got done by the department at the risk and cost of the contractor. The decision of the Electrical Engineer in this regard shall be final & binding on the contractor.

13) The successful tenderer should furnish well in advance three copies of detailed instructions and manuals of manufacturers for all items of equipment’s regarding installation, adjustments, operation and maintenance i/c preventive maintenance and troubleshooting together with all the relevant data sheets, spare parts, catalogue and workshop procedure for repairs, assembly and adjustments etc all in triplicate.

14)   Dispute Resolution: If any dispute with regard to the terms of this Contract shall be handled through Arbitration, as per the following terms, between them:

(I) THAT, the parties agree that any dispute or difference whatsoever arising between them out of/under or in connection with or relating to the existence, meaning, scope, validity, termination, breach, or any other effect flowing from the Contract shall be referred to a Sole Arbitrator, as appointed under clause (IV) herein below;

(II) AND THAT, the parties agree that in respect of those matters, as are not defined in the terms and conditions of this Dispute Resolution Clause, or anywhere else in the Contract, the same shall be decided and settled by the Sole Arbitrator, in accordance with the Arbitration and Conciliation Act, 1996 and the amendments thereof as in operation on the date of execution of the Contract;

(III) AND THAT, the parties agree that the place of Arbitration shall be at Jaipur, Rajasthan.

(IV) AND THAT, whenever the parties decide to resort/resolve to Arbitration for dispute resolution, the Director, LNMIIT shall be the authority to appoint the Sole Arbitrator, and such appointment shall be binding on both the parties:

Provided that before approaching Director-LNMIIT for appointment of Sole Arbitrator, the parties shall make a sincere attempt to resolve their dispute, within a time period of 2 months, through mutual conciliation/ negotiations. The sole arbitrator shall not be an employee of any of the party to this tender.

(V) AND THAT all costs relating to the Arbitration proceedings shall be borne equally by both parties.

(VI) AND THAT, the parties agree that the language for making all submissions and evidence will be presented in ENGLISH during the proceedings.

(VII) AND THAT, it is agreed between the parties that they shall extend their fullest support and co-operation to the Sole Arbitrator and not seek adjournment of the Arbitration proceedings, without explaining the reasons therefore, in writing, in advance, for seeking of such adjournment, and further that there shall not be more than two such adjournments granted, even when there exists a valid reason for seeking such adjournment. And, it is further agreed that the parties should cooperate in completing the arbitration process and the broader dispute resolution within 6 months or at most with an extension, on mutual consent, of another 6 months.

(VIII) The sole Arbitrator shall record, in writing, the arguments of the two parties on each of the points of dispute and pass a reasoned and speaking Award thereon, within the Terms and Conditions of the Contract Agreement.

(IX) If any difference remains after an Arbitral award, and an appeal could be raised under the Arbitration and Conciliation Act, 1996, the appropriate Court within the Jaipur , Rajasthan shall deal with the matter.

TECHNICAL SPECIFICATIONS FOR ELECTRICAL WORKS

FOR HT/LT SUB-STATION WORKS OIL TYPE TRANSFORMERS

Scope

The specification covers the design, manufacture testing and inspection before dispatch and delivery at site.

The specification covers oil immersed, naturally air cooled, outdoor type, three    phase, 50 Hz,  33000V/0.433V and 33000V/11000V step down Power transformers.

Applicable Standards

- Unless   otherwise modified in the   specification, the transformers shall comply with  the requirement  of  ISS:2026  (latest issue) and REC specification 2/1973 and ISS:2099 (latest  issue).  The bushings used shall conform to ISS: 2099 (latest issue) except as modified herein.

- Type:  The transformers shall be double wound, three phase oil immersed, oil natural cooled (type 'ON', core type suitable for outdoor installation in  tropical climate and shall  be  insulated  with  DPC insulation  on HV and LV windings.

- Design and Standardization

The transformers and accessories shall be designed to facilitate operation, inspection, maintenance and repairs. All apparatus shall also be designed to  ensure satisfactory  operation under such sudden variations of load  and  voltage  as may be  met  with  under  working    conditions  on the system, including those due to  short circuits.

The design shall incorporate every reasonable precaution and provision for the safety of all    those concerned in the operation and maintenance of the equipment keeping in view the requirement of Indian Electricity Rules.

All material including brought out items like  bushings, oil  radiator, conductor and insulating  materials  used shall  be  of  the best  quality and of  the  class  most suitable for working under the conditions specified  and  shall  withstand  the  variation  of  temperature   and   atmospheric conditions arising under working  conditions without undue distortion or deterioration  or setting up of undue stresses in any part and also without affecting the  strength and suitability of the various  parts  for  the work which they have to perform.

Corresponding parts liable to replacement shall be interchangeable.

Cast iron shall not be used for chambers of oil filled apparatus or for any part of the equipment which is in tension   or subject to impact, stresses or   where corrosion due to acidity on sludging is likely to occur.  This clause  is  not intended to prohibit the  use  of suitable  grades  of cast iron for parts  where  service experience  has shown it to be    satisfactory  e.g.,  large valve bodies.

All outdoor apparatus, including bushing insulators with their mounting shall be designed so as to avoid external pocket in which water can collect and internally air could trap.

All taper pins used in any mechanism shall be of the split type complying with IS: 2593 for these items.

All connections and contacts shall be of ample  section and  surface  for carrying  continuously  the  specified currents  without heating and fixed connection shall  be  secured by bolts or set screw of common size  adequately locked  against  vibration. Lock nuts shall be used on stud connections carrying current.

All apparatus shall be designed to minimize the risk of accidental short circuit caused by animals, birds or vermin.

All transformers shall be capable of operation continuously in accordance with IS loading guide at their continuous maximum rating and at any ratio without exceeding, temperature rise.

Oil

Transformer oil to be used for first filling shall comply with the specification indicated hereunder, generally as per IS: 335 of 1983 (Third revision) and REC specification No.39/1985 except in so far as values indicated separately as per Board's specification for EHV Grade Oil.

- The tenders must clearly specify whether the losses quoted are FIRM or subject to IS tolerance. In case of any ambiguity, loading as per IS tolerance shall be considered for price comparison purpose.

- The purchaser reserves the right to reject any transformer, if during tests at supplier's works, the tested no load losses and total   losses, exceed the corresponding maximum guaranteed losses by more than the following values:

- Owner reserves the right to test any one transformer, selected at random out of the transformers offered for  inspection/supplied, in  any  independent  laboratory  of national repute, preferably CPRI, for the purpose of routine tests as per IS 2026. The entire expenses for the same shall be borne by the contractor.

Terminal Arrangement

The transformers shall be fitted with HT cable connectors on HV side and bus-bar connections on LV side.

The bushings  shall be filled with transformer oil, EHV grade, which shall be of non-oil

communicating type with small aperture   of 2mm diameter.

The HV/LV bushings shall have the characteristics as per IS: 2099 (latest issue).

The electrical characteristics of bushing insulators shall be in accordance with IS: 2099 as amended from time to time.  All type and routing tests shall be carried out in accordance with IS: 2099-1973. The test voltages for various tests as stipulated in IS: 2099-1973 are below:

Dimensions of the LV 12 bushings including neutral (LV side) shall conform to IS: 3347 (Part-III) and those of the 36 KV bushing (33 KV side) shall conform to IS: 3347 (Part-V).

Vibration and noise

- Every  care  shall  be  taken  to  ensure  that  the  design   and manufacture all  transformers and accessories shall be such  as  to reduce  noise  and  vibration  to the level  obtained  in  good  modern practice.

- The manufacturers will ensure that the noise level shall not be more than 5 Db above the NEMA standard publication TR-1.

Flux density: Over fluxing

- However, in case of transformers with variable flux, the voltage variation which would affect flux density at every tap shall be kept in view while designing the transformers.

Internal earthing arrangement

(I) 	General:

All metal parts of the transformer with the exception of the individual clamping plates shall be maintained at some fixed potential.

(II) 	The top main core clamping structure shall be connected to the tank body by a copper strip. The bottom clamping structure shall be earthed by one or more of the following methods.

- By connection through vertical tie rods to the top structures.

- By direct metal to metal contact with the tank base maintained by the weight of the core   and the windings.

- By a connection to the top structures on the same side of the core as the main earth connection to the tank.

(III) 	Size of Earthing Connections

All earthing connections with the exception of  these  from the  individual  cell  clamping rings  shall  have  a  cross  sectional  area  of not less  than  0.8  sq mm. Connections inserted between laminations of different section of core as per lause-17 III (B) shall have a cross sectional area of not less than 0.2 sq mm.

(IV) 	Leads from winding to bushing and internal connection

The  leads from winding to bushing and internal connection should  be  rigid  enough to winding  normal  vibration  and transportation   shocks  and  short  circuit  stresses.  They should be spaced in such a way that necessary clearances are maintained not only in air but with oil medium at the lowest electrical strength as per relevant ISS over the period of normal service.

Guarantee:

The manufacturer  shall among other things   guarantee   the following:

(I)  	Quality and strength of material used, both electrical and mechanical.

(II)  	Satisfactory operation during the guarantee period of 60 months from the date of receipt of Stores. This period  will be  reckoned  from  the day  all  accessories  are  received enabling  assembly  testing, commissioning  and  commercial operation of transformers.

(III) 	Performance figures are to be supplied by tender in the schedule   of   guaranteed particulars.  In   schedule   of 'GUARANTEED TECHNICAL PARTICULARS', all details as required in IS: 2026 shall be given.

Wheels and Axles

The transformers shall be provided with bi-directional flat roller.

Fittings & Accessories:

The following standard fittings as given below:

The fittings  shall  be  in accordance  with  the  details to the extent these  area  specified  in IS:2026.

- Inspection cover

- Rating plate

- Diagram plate with tap position and relative   HV/LV voltage.

- Two earthing terminals.

- Lifting lugs.

- 4 jacking pads.

- Conservator with top fill up cap and bottom drain valve.

- Dehydrating breather of required sizes.

- Connecting pipe with valve and Buchholz relay.

- Radiator with top air release plugs and connected valves top and bottom for connection to main tank.

- HV - 3 bushings

- LV - 4 bushings

- On load circuit tap switch with lock and 2 keys

- Mercury Thermometer

- Thermometer (dial type) with one contact for alarm

- Thermometer pocket

- Magnetic oil level gauge indicating three position of  oil marked.

- Oil filling hole and cap

- Air release device on tank top

- Pressure relief device through explosion vent diaphragm with fresh equalizer pipe air release plug.

- Gas and oil actuated relay.

- 2 filter valves (top valve, lower valve to be used also as drain valve).

- First filling of oil.

S C H E D U L E - I

| 1. | Rating and terminal marking plate: Following details are to be given on the name plate: |  |
| --- | --- | --- |
|  | i) Name of the manufacturer |  |
|  | ii) Order No. and date |  |
|  | iii) Rating of transformer and voltage ratio |  |
|  | iv) Year of manufacturer |  |
|  | v) S. no. of transformer |  |
|  | vi) Max. guaranteed losses (a) No load losses (b) Load Losses |  |
|  | viii) Type of coating |  |
|  | ix) HV/LV Amps |  |
|  | x) Percentage impedance |  |
|  | xi) Maximum temperature rise Maximum winding temperature |  |
|  | xii) Weight of transformer (a) Core and winding - Kg. (b) Weight of oil - Kg. (c) Total weight - Kg. (d) Oil (Total) - Liter |  |
|  | xiii) Tap positions and corresponding voltage on HV and LV side |  |
| 2 | Earthing terminals - 2 Nos. |  |
| 3 | Tank lifting lugs - 2 Nos. |  |
| 4 | Packing pads - 4 Nos. |  |
| 5 | Silica gel Dehydrating Breather (with one kg. minimum gel content) |  |
| 6 | Conservator with oil filling cap, drain valve with plug and magnetic oil level gauge with alarm contacts. The oil level gauge shall have three positions of oil. |  |
| 7 | Pressure relief device through explosion vent diaphragm. |  |
| 8 | Gas and oil actuated relay with 2 contacts. |  |
| 9 | Thermometer (dial type) with one contact for Alarm. |  |
| 10 | Filter valves top and bottom (lower valve to be used as drain valve which should be able to drain oil completely). |  |
| 11 | Air release device |  |

Before installing, the accuracy of the temperature indicators shall be checked by hot oil or water bath. The switches shall be adjusted   to make contacts at the desired temperatures depending upon the site conditions i.e. ambient temperature loading conditions etc. The    capillary tube shall be protected adequately to withstand all normal handling. It should not however be bent sharply or repeatedly and should be supported by clips to prevent sagging. On no account it shall be cut. The thermometer pocket shall be filled with sufficient      transformer oil to ensure good thermal contact between the pocket walls and the thermometer bulb.

Bare  conductors  of  copper or  aluminum  as  directed  by Engineer-in-Charge  shall  be used for connections to  the  transformer terminals.  These may be of flexible type or the rigid type having rectangular or hollow circular cross-section. Where  connections  are rigid  and  more than 3 to 4.5 meters long special  expansion  type  of  connectors  are  recommended  to prevent the  terminal  bushings  being  unduly  stressed  due  to thermal expansion. For aluminum or ACSR  conductors  used for connections to the transformer  terminals  made  of  copper,  suitable  bimetallic  type of connectors  should  be used to prevent electrolytic corrosion at the contact surfaces of dissimilar metals and necessary precautions taken in making these joints.

The transformer should be so installed that there is no risk of anyone receiving an electric shock. Although, with all metal  parts  of the metal tank bonded together and properly earthed the tank may  be  considered  quite  safe,  yet  consideration should  be  given  to  the arrangements of the connections.

SWITCH BOARDS (CUBICAL TYPE)

The switch board shall be metal clad, totally enclosed, single front, floor mounted, cubical type for use on 415 volts 3 phase, 50 cycles system with a fault level withstand of 50 K A RHS symmetrical. The switch board shall be made up of the requisite vertical sections. Which when coupled together shall form continuous dead front switch boards of dust and vermin proof construction.

All panels and cover shall be properly fitted and square with the frame. Holes in the panel shall be correctly provided and tapped into on adequate thickness of metal or provided with nuts, for convenient fixing of screws. Self threading of screw shall not be used in the fabrication of the panels. All doors shall be provided with neoprene gaskets. Each vertical panel structure shall contain a cable way alloy of adequate width with provision for suitable cable supports. The cable compartment shall have hinged door. There shall be a separate gland plate for each cable entry so that there will not be dislocation for already wired circuits when new feeders are added. The entire switch board shall be factory assembled.

The panel shall include the required number of MCB / FSU and breakers as per item, copper bus bars as per requirement and item of work with separate neutral bar & earth bars of coppers.

The units should be arranged in their formation to provide a compact switch board having a pleasing appearance. The minimum depth of switch board shall be 300mm. Steel sheet hinged lockable doors shall be duly interlocked with fuses witch unit to prevent opening of the panel when the switch is in 'ON' position. Safety interlocks shall be provided also. All the MCCB's shall be provide with vertical operation.

All indicating instruments shall be of the flush mounting industrial pattern conforming to the requirement of IS: 1248, indicating lamps shall be of the neon type. Separate compartment shall be provided for accommodating instruments, indicating lamps, control contractors and fuses etc. these shall be accessible for testing and maintenance without any danger of accidental contact with line parts of the circuit breakers, unit’s bus bar and connections.

Horizontal wire way with screwed cover shall be provided at the top to take interconnecting control wiring between different vertical sections. Control wiring shall be of copper conductor and shall be color coded for easy identification of circuits. This should be of not less section than 2.5 sq mm not more than two connections shall be made off anyone terminal.

All cable shall be neatly bunched and shall be secured to wiring cradles. All outgoing cables shall be fitted with identification ferrules at each end. Circuit diagram showing the arrangement of circuits shall be pasted on the inside of panel door and covered with transparent plastic sheet. Knockout holes of appropriate size and number shall be provided with panel in conformity with the location of incoming and outgoing cables/conduits. Facility shall be provided for termination of cables from both above and below the panel. Where cables enter from below, cable eyes shall be provided for connections to main earth. The earth bar shall run within the base frame.

All steel material used in the construction of the switch board should have undergone a rigorous rust proofing process comprising alkaline degreasing, desiccating in dilute sulfuric acid and recognized Phosphating process. The steel work should then receive the coats of oxide premier before final coat of staying synthetic enamel paint of approved shade.

Engraved plastic labels shall be provided indicating the feeder details. Danger notice plate shall also be provided as per I.E. Rules. Adequate provision shall be made for escape of hot gases by providing louvers. The louvers shall be located as to direct the hot gases away from the operating personnel and shall be covered with a perforated sheet having less than 1 mm diameter perforations to prevent entry of vermin. All nuts, bolts and washers shall be cadmium plated. Each panel incomes section shall be provided with voltmeter 0-500 volts with 3-way on and off selector, switch, ammeter of appropriate range with selector switch as per the bill of material in the tender.

L.T. CABLE

L.T. cable shall be of aluminum/copper conductor as instructed by project engineer / Project-in-charge, FRLS type PVC insulated, PVC sheathed steel tape armored construction conforming to IS- 1554 of 1100 volts grade. The aluminum conductors shall be stranded for sizes above 16sq mm and sector shaped standard conductors shall be used for heavy sizes. As far as possible, cables shall be supplied in drums. Cables supplied shall bear manufacturer's identification marks at regular intervals.

CABLE TERMINATIONS

Cable leads shall be terminated at the equipment terminals by means of crimp type soldieries connectors as manufacture by MIS. Dowel Electro works. Crimping shall be done by hydraulically operated tools and conduction jelly shall be applied. On the conductor Insulation of the leads should be removed immediately before the crimping. Conductor surface shall be cleaned and shall not be left open for long, prior to crimping to prevent oxidation. Control cables of single strand cables may be directly terminated on to the terminals. Straight through joint if required shall be made by rising epoxy resin cold setting compound type Tripoli of M seal brand. Compression brass cable gland wherever used shall be of current size for cable and terminations. No oversize cable glands shall be used. The gland must grips the armor of the cable firmly, so that in the event of ground movement no undue stress is transferred to the cable conductors. The gland must establish good electrical contact between cable armor, lead sheath and body of switcher. Identification ferrules indication the circuit shall be used for incoming and outgoing cables.

CABLE WORK IN UNDER GROUND

While laying underground cables care should be taken so that any underground structure such as water pipes, sewerage lines, etc. are not damaged. Any telephone or other cable coming in the way shall be properly protected as per instructions of Architect. All cable routes shall be carefully measured and cable cut to the required lengths leaving sufficient length for the final connection of the cable. All cable trenches entering sub-station plants etc. shall be effectively sealed after installation of cables to avoid entry of water.

The L.T. cables shall be laid not less than 75 cm below ground level in a trench 35cm wide minimum .The depth of the trenches shall be uniform throughout. A bed of 17 cm dry sand shall be load before he cable is laid.

When the cable is properly straightened and laid in the trench, it should be covered all around 8mm thick layer of sand. Approved cable indicators shall be fixed at suitable distances along the route of the cable.

Unless otherwise specified the cables shall be protected by second class bricks of not less than 22.5x 10.0x7 cm or stone tiles or any other approved material placed on sides and top of the cable to form a channel throughout the length.

Spun reinforced concrete pipes shall be provided for all road crossings. The size and nature of the pipe shall be decided by Architect and shall not be less than 10cm in diameter for a single cable and not less than 20cm for more than one cable. These pipes shall be laid in the ground with 10cm thick bed of cement concrete 1:5: 1 0 and may be loose jointed. The top surface of pipe shall be at minimum depth of 90cm from the ground level when laid under the roads/ pavements.

Filling of trenches shall be done after the sand cushioning and laying of tiles are carried out to the satisfaction of a architect, where road bergs or lawns have been cut of Keri stones displaced the same shall be repaired to the satisfaction without any extra cost.

CABLE WORK

LAYING OF CABLES OVER DUCTS/ WALL/TRAYS:-

Cable ducts should be of such dimension that the cables laid in it do not touch one another .If found necessary the cable shall be fixed with clamps on the walls of the duct .Cables shall be laid on the walls/on the trays as required using suitable clamping/ fixing arrangement as required. Cables shall be neatly arranged on the trays in such manner that cross-crossing is avoided and final take off to switch gear is easily facilitated.

All cables will be identified close to their termination point by cable number as per circuit schedule. Cable numbers will be punched on 2mm thick aluminum strips and securely fastened to the cable. In case of control cables all covers shall be identified by their wire numbers by means of PVC ferrules. For trip circuit identification additional red ferrules are to be used only in the switch gear/ control panels, cables shall be supported so as to prevent appreciable sagging. In general distance between supports shall not be greater than 600mm for horizontal run and 750mm for vertical run.

TESTING OF CABLES:-

After laying and jointing work is completed, a high voltage test should be applied to all cables to ensure that they have not been damaged during or after the laying operation and that there is no fault in the jointing. For 33KV XLPE cable high pot test shall be done at site by 50KV system and nothing extra shall be payable. Cable for use on low and medium voltage system (1.1 K V grade cables) should with stand for 15 minutes a pressure of 3000 volts DC applied between conductors and also between each conductor and sheaths .In the absence of " Pressure testing facility" it is sufficient to test for one minute with a 1000 volts insulation tester In case, the test results are unsatisfactory the cost of all repairs and replacement and relaying will be made good by the contractor. Nothing shall be payable for conducting high pot test.

CABLE TRAYS:

Cable trays shall be ladder type fabricated out of mild steel/ slotted angles and flats of required width as per design. Bends shall be prefabricated the cable tray shall be primed and painted with two coats as approved by Engineer - In - Charge. Suitable provision shall be made where a tray crosses expansion joints. The width of the tray shall allow for a suitable separation between cables the design shall allow for adequate bending reduces for the sizes of cables.

The tray shall be suspended from the sophist of the concrete slab by means of approved steel hangers spaced at a distance of not more than 100cms. Suitable bushes shall be provided where cables pass through apertures in the tray. Cable must securely fixed to the tray with fasteners.In routing, necessary barriers and spacing shall be maintained for cables of different voltages in case they lie side by side. Telephone cables shall cross the power cables only at about right angle and these two shall not run in close proximity. Full details of the tray shall be approved by the site engineer before fabrication. Earth continuity shall be maintained between each section of cable tray and each total run of tray shall be effectively bonded to the nearest earth continuity conductor. AII nuts and bolts used shall be of galvanized steel.

EARTHING

All non-current carrying metal parts of electrical installation shall be earthed as per IS:3043-1986 with latest amendments. All metal conduits, cable sheathes, switch gear, DB's, light fixtures, equipments and all other parts made of metal shall be bonded together and connected to earth electrodes. Earthling shall be in conformity with provision of rules 32, 61, 62, 67& 68 of Indian electricity rules (1956).

All earthing conductors shall be of high conductivity copper, GI and shall be protected against mechanical damage. The cross sectional area of earth conductors shall not be smaller than half that of the largest current carrying conductor. However the contractor shall use the sizes specified in the bill of quantities.

- All fixtures and socket outlets, fans, switch boxes and junction boxes, etc. shall be earthen with bars copper wire as specified in the item of work. The earth wire ends shall be connected with solder-less bottle type copper lugs.

- All single phase DB's up to 60Amps shall be earthen with 8 SWG GI wire as per item of work.

- All 3 phase switch boards up to 100Amps rating shall be earthen with 2Nos. Separate and 25 x 3mm GI strip as per item of work.

- All switch boards of ratings more than 100Amps and above shall be earthen with 2Nos. Distinctive separate 25 x 6mm GI strips as per item of work.

- All the earth wires in switch boxes, DB's and light fixtures/fans shall be provided with green color sleeving.

Main earth bus shall be taken from the LTSwitch board to earth electrodes. The electrical resistance of earthing conductors shall be low enough to permit passage of fault current necessary to operate fuse or circuit breaker and shall not exceed 2 ohms.

PLATE EARTHING

The earthing electrode shall consist of GI plate (60cm x 60cm x 6mm) tinned copper plate 60cm x 60cm x 3mm) as specified in item of work. Galvanizing of the plate shall conform to relevant Indian Standard. The plate electrode shall be buried in the ground with its faces vertical and top not less than 4.5m below GL. The earth plate pipe shall be buried in the ground below the permanent moisture level but not less than 4.5m below ground level. The plate shall be filled with charcoal dust and common salt filling extending up to 15cm around it on all sides. There shall be a 20 mm dia., medium class GI pipe running from top plinth plate up to the ground level for watering pipe. The top of the pipe shall be provided with a funnel and a GI mesh screen for washing the earth. This will be housed in a masonry sump with cement plastering not less than 30cm deep. M.S. Frame heavy duty with hinged cover and locking arrangement shall be suitably provided over the sump. The earthing link from electrode onwards shall be suitably protected from mechanical injury by GI pipe. The portion of this protection pipe within the ground shall be buried at the least 30cm deep (to be increased to 60cm in case of road crossing and pavements). The portion within the building shall be recessed in walls and floors to adequate depth. In the case of plate earth electrode, the earthing load shall be securely bolted to the plate with two bolts, nuts check nuts and washers. In case of pipe earth electrode, it should be counted by means of a 'through' connection with the earth lead with electrode shall be GI brass in case of copper plate electrode.

The electrical resistance of earthing conductors shall be low enough to permit passage of fault current necessary to operate the fuse or circuit breaker and shall not exceed 2 ohms.

PIPE EARTHING

The earthing electrode shall consist of GI pipe of 40 mm dia. and 4.5m length B-class or as described under schedule of quantities. Galvanizing of the pipe shall conform to relevant Indian Standards. The top of the pipe shall be provided with a funnel and a GI screen for watering the earth. This will be housed in a masonry sump not less than 30 cm square and 30 cm deep. A heavy duty MS frame with hinged cover and locking arrangement shall be suitably provided over the sump as approved by the Engineer in-charge.

GI pipe electrode shall be cut tapered at the bottom and provided with holes of 10 mm dia., drilled not less than 7.5cm from each other. The pipe shall be buried in the group vertically with its top not less than 20cm below ground level. The earthing lead from electrode onwards shall be suitably protected from mechanical injury by GI pipe within ground and the portion within the building shall be recessed in walls and floors to adequate depth. The earthing lead shall be connected by means of a through bolt, nuts and washers and cable socket. All materials used for connecting the earth lead with the electrode shall be GI The earth pit depth shall not be less than 4.8 m. No earth pit shall be fixed within 2m of a wall or foundation. Efforts shall be madetolocate them in grass lawns or near flower beds or water taps. The distance between two earthing stations shall be at the least 2m.

SPECIAL CONDITIONS

- All electrical work shall be carried out in compliance with specifications given hereunder in this section and in compliance with Indian Standard specifications and Indian Electricity Act and Rules in force. The works shall also conform to any special requirement of Local State Electricity Board. If any case, the above-mentioned rules, regulations etc. are not in accord, the division of the consultant Engineer-in-charge regarding rules to be followed or manner of execution of work shall be final and binding. The work shall be executed under the direct supervision of person holding a certificate of competency issued by the State Government (Chief Electrical Inspector) for the type of works involved in conformity with the best methods of modern engineering practice and to the entire satisfaction of the Consultant / Engineer-in-Charge. The contractor has to submit the test report at various stages of completion as per requirement of the client.

1.1	Work shall be executed through licensed electrical contractor approved 	bytheOwner /Architect /Electrical Inspect (Directorate of safety, Govt. of India)

1.2 		These special conditions of contract shall be read in conjunction with theGeneralConditions of Contract, Schedule of Quantities, Technical Specifications, Drawings and other documents relating to the work and shall have preference over laid down general conditions and specifications.

1.3 		Notwithstanding the sub-division of the documents into these separate sections and volumes, every part of each shall be deemed to be supplementary and complementary to every other part and shall be read with and into the contract, so far as it may be practicable to do so.

1.4 		The contractors shall mobiles and employ sufficient resources to achievethedetailed schedule with in the broad frame work of the accepted methods of working and safety. The contractor shall provide everything necessary for the proper carrying out of the work, including tools, plants and other materials.

1.5 	No additional payment will be made to the contractor for any multiple shiftworkorother incentive methods contemplated by him in his work schedules even though the time schedule is approved by the consultant /Engineer-in-Charge.

1.6 		The work shall be executed as per the programmer drawn or approved bytheConsultant and it shall be so arranged as at site. No claim for idle labor shall be entertained nor shall any claim on account of the delay in the completion of the building work to be tenable except extension of time secured by the contractor as stated elsewhere.

1.7 	The contractor shall permit free access and afford normal facilities and usual conveniences to other agencies or departmental workman to carry out connected work or other work services under separate arrangements. The contractor will not be allowed any extra payment on this account.

1.8 		All soil, filth or other matter of any offensive nature taken out of any trench, sewer drain, cesspool or other place shall not be deposited on the surface, nut shall at once at carted away by the contractor free of charge to a suitable pit or place to be provided to him.

1.9 		The contractor shall provide all equipments / instrument labor and such other assistance required, by the Engineer-in-Charge for measurement of the work, materials etc.

MATERIALS

All materials, equipment's, fittings and fixtures used in electrical works shall conform to the attached list of approved make of materials.

All material shall be new, soundly and robust in construction and well finished. Surplus material after completion of work shall be taken back by the contractor and the cost shall be recovered if the advance payment has been made earlier by the client.

Unless otherwise stated in the conditions of contract, of contract, samplesofallmaterials, fittings and fixtures to be supplies by the contractor shall be submitted to the consultant for his approval. The contractor shall not commence the work until the samples are approved, in writing from the consultant.

The contractor shall ensure that all the materials incorporated in the workareidentical in all respects with the approved sample. All samples notdestroyedintesting shall be returned to the contractor after completion of contract. No payment shall be made for samples destroyed in testing.

CLARIFICATIONS OF DISCREPANCIES

4.1 	In case of any discrepancy between specifications and drawings etc. or disputes in respect, the interpretation and decision of the Engineer/ project-in-Charge shall be final and binding.

MISCELLANEOUS

5.1	After completion of the work the whole installation shall be tested by the contractor in the presence of the Engineer/ Project-in-charge. The tests shall comply the following I.E.E. Regulations and shall be submitted along with the final bill.

- The result of the insulation test shall comply with the I.E.E. Regulations1101to11 08A and 1008 b, as may be applicable.

- Test shall be carried out to ascertain that all the non-linked SP switches have been connected to the phase conductor.

- The continuity test of the earthling system shall comply with I.E.E. Regulations 1108 to 11109 to the latest addition.

If the results of the above tests does not comply with the I.E.E. Regulations,thecontractor shall be bound to rectify the faults so that the required results are obtained. The contractor shall be responsible to provide all the necessary testing instruments, such as megger, insulation tester, earth tester, multi meter, AVO meter etc. for carrying out the above tests. 10% of the installation cost will be deducted from the bill if the IR and earth resistance tests not carried out in presence of Engineer-in- Charge.

5.3 	The work will not be considered as complete and taken over by the Employer till all the components of the work after being completed at site in all respects have been inspected / tested by the Engineer-in-Charge to his entire satisfaction and a completion certificate issued by the Owner’s Representative/Project Engineer/Project-in-Charge to this effect.

5.4 	At the completion of the work and before insurance of certificate of virtual completion, the contractor shall submit 3 set of as built drawings with one reproducible of each drawing to Consultant layout drawingsdrawnatapprovedscale indicating the complete wiring / cabling / earthling system as installed.

5.5 	The contractor will submit a detailed schedule of program of work, on demand of Owner’s Representative/Project Engineer/Project-in-Charge.

WORK AND WORKMANSHIP

6.1 	The work shall be of the highest standard, both as regard its design and workmanship. Modern tools and first class, latest techniques shall be employed for its execution.

6.2 		Any damage done to the building during the execution of work shall be responsibility of the contractor and it shall be made good by him, at his cost, to the entire satisfaction of the Owner’s Representative/Project Engineer/Project-in-Charge.

6.3 		All electrical work shall be executed by skilled electricians under the direct supervision of whole time, fully qualified licensed electrical engineers and supervisors. The contractor shall produce requisite evidence regarding the qualification of the engineer, supervisors and other workers.

6.4 	The contractor shall possess all the relevant and valid licensed as per the regulations of the Indian Electricity Rules and the Local Electrical Inspector's requirements.

6.5 	The work shall have to be coordinated with the building work and other allied jobs/trades to the entire satisfaction of Engineer-in-Charge/Consultant.

CERTIFICATE OF INSPECTION

7.1 	Complete scheme drawing for equipment's/earthling/cable layout/schematic drawing and other details as per requirements shall be prepared by the contractor and got approved by Owner’s Representative/Project Engineer/Project-in-Charge, before commencement of work. Nothing shall be payable to contractor on this account.

7.2	The contractor shall be responsible for getting the installation inspected and approved by the Electrical Inspector and other, local electric supply company, if required.

7.3 	The contractor shall obtain and deliver to Owner’s Representative/Project Engineer/Project-in-Charge the certificate of final inspection and approval of the local electrical authorities concerned. The inspection fees etc. shall be borne by the contractor.

7.4 	In case of any defects are pointed out by the CE Electricity Authority Inspector, the contractor shall remove these defects at his own cost and arrange for re-inspection or inspection by the electrical inspector, till such time the installation is finally approved and the required certificate is issued. The contractor shall bear all expenses and deposit the necessary fees for subsequent inspections by the CEA.

7.5 	Owner’s Representative/Project Engineer/Project-in-Charge shall have full powers to get the material or workmanship etc inspected and tested by an independent agency, at the contractor's expenses in order to ascertain their soundness and adequacy.

7.6 	The contractor shall be responsible for obtaining all necessary approvals for entire scheme from State Electrical Board before commencement of the work. All coordination with SEB shall be responsibility of contractor till commissioning and getting electricity in the complex and finally handing over the installation.

7.7 	The contractor shall possess State Electrical Contractor's license and all the relevant and valid other licenses as per the regulations of the Indian Electrical Inspector's requirements.

7.8 	Any amount to be deposited with the State Electrical Board shall be deposited by the contractor after observing necessary formalities required and take all follow up action for the same. However, the amount so deposited by the contractor will be reimbursed to the contractor on production of necessary and adequate documentary proof/records.

7.9 	Working drawing for all system shall be prepared by the contractor & gotapprovedbefore starting of the work. (H.T. Panel / transformer / LT Panel & Sub Panel / Bus duct and Rising main)

LIST OF APPROVED MAKES OF MATERIALS

|  | TRANSFORMER | CROMPTON GREAVES/ABB/Voltamp |
| --- | --- | --- |
|  | VCB HT PANEL | CROMPTON GREAVES/SEIMENS/ABB/ SCHNEIDER |
|  | HT CABLE | POLYCAB/ HAVELLS |
|  | CONTROL CABLE | POLYCAB/ HAVELLS |
|  | SOLDERLESS LUGS / FERRULES | LAPP /DOWELL |
|  | CABLE GLANDS | LAPP /COMET |
|  | L.T. SWITCH BOARD | L&T/SCHNEIDER |
|  | L T. CABLE | POLYCAB/HAVELLS |
|  | ACB / MCCB | L&T / SCHNEIDER |
|  | 11000 VOLTS CABLE LOINTS | RAYCHEM / ANY EQUIVALENT / CABLE GLANDS / CABLE LUGS / DOWELLS |
|  | METERING ARRANGEMENT | L & T /CONZERV / SECURE |
|  | INDICATINGLIGHTS, SELECTOR SWITCHES PUSH BUTTONS, ETC | L &T / CONZERV |
|  | PROTECTION RELAYS | GE POWER CONTROLS /AVKSEGC / CSPC |
|  | MCB | LEGRAND |

NOTE: Above makes of equipment are approved subject to their meeting the specifications.

The contractor, however, shall seek approval of specific make from Engineer-in-Charge before commencing the work. The decision of the Engineer-in-Charge shall be final & binding on the contractor in their respect.

TECHNICAL SPECIFICATIONS –

HT CABLES 33 kV and 11 KV GRADE XLPE INSULATED  MULTICORE CABLES - EARTHED

1.	GENERAL

Cables shall be aluminum conductor, XLPE insulated, PVC sheathed, Armoured/ and shall be supplied, inspected, laid, tested and commissioned in accordance with drawings, specifications, relevant Indian Standard Specifications and cable manufacturer’s instructions.

2)

- Conductor:

- Material: Aluminium

- Shape: Stranded compacted circular aluminium/ copper as per Class-2 of IS: 8130.

- Conductor Screening: Extruded semi conducting compound.

- Insulation material: Cross linked polyethylene (XLPE) (Red, Yellow, Blue)

- Insulation screening: Extruded semi conducting compound followed by helically wrapped 0.050mm thick copper tape.

- PVC Fillers

- Inner Sheath: Extruded PVC

- Armouring: Single layer of galvanized steel round wires/ flat strips

- Outer sheath: HR PVC type ST-2 of IS: 5831

- Colour of sheath: Black

3.	TESTS

Cables shall be type tested and routine tested in accordance with IS: 7098 (Part II):

a. 	Conductor resistance test.

b. 	Partial discharge test.

c. 	High Voltage test.

The following tests shall be carried out at site for insulation between phases and between phase and earth before and after cable laying:

a. 	Insulation Resistance Test.

b. 	Continuity resistance test.

c. 	Sheathing continuity test.

d. 	Earth test.

e. 	High Voltage test.

Schedule of Quantities for Supply, Installation, Testing and Commissioning of Upgradation Work from 11 kV to 33 kV for External Electrical HT Panels, Cabling and Transformer Work for JVVNL DS – HT Metering & Indoor Distribution 33 kV System

UPGRADATION WORK: 11 kV → 33 kV SUBSTATION _ External Electrical Works HT Panel, Cable and Transformer

| S.No. | Item Description | Qty | Unit |
| --- | --- | --- | --- |
| 1 | SITC of Indoor Type Floor mounted metal clad 33 KV,1250 Amps 3 phase, 50 Hz Vacuum Circuit Breaker (VCB) as per IEC 62271-1,100,200, IS- 13118 Standard made from Powder painted pre-fabricated, CRCA sheet steel /High quality Aluminium-Zinc (Aluzinc) coated sheet steel. Fabrication shall be done through CNC turret press and CNC bending machine having a rupturing capacity of 500 MVA, 26.3 KA breaking capacity for 3 sec, Internal arc type tested for 26.3KA for 1 sec with AFLR classification totally enclosed with Copper bus bar of 1250 Amps for each phase, flush front, Horizontal isolation, Horizontal draw out type with Electrical and Mechanical interlock and automatic safety shutter gear including padlocking arrangement, isolation plugs, assembly of 4 vaccum interrupters , with each pole individually encapsulated by epoxy insulations to make it dust proof and self - aligning finger type isolating contacts, truck having integral racking with necessary interlocks (for insertion and removing of VCB), manual and automatic motor charged independent closing/ tripping spring , trip free operating mechanism with closing and tripping push buttons and mechanical breaker. Interconnected with HT sleeve bus bar of 1250 Amps , Basic Insulation level (BIL) : 36KV (RMS) / 170KV (Peak) and Altiude less than 1000 meters, including all protection, indication, Operation, monitoring and control and accessories etc. as required. .Factory Tests of VCB panel as per OEM's QAP in it's own Manufacturing facility shall be witnessed by department Engineer virtually / Physically. All as per pre-approved by Engineer in charge."2 Incoming 2 Outgoing One Bus Coupler Panel comprising of Side cable box & Transformer Auxiliary protection and comprising of following. MAKE: SEIMENS/ABB/SCHNEIDER - VCB 1250 Amps . VI of VCB should be sealed for 30000 operations. VCB operating mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continuous rating to achive minimal failure. - Resin Cast type CT having Ratio : 400-200A/ 1-1 A, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA (How ever CT Ratio shall be decided as per load requirement) - VT Ratio: 33KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selector switch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. " | 1 | Nos |
|  | ELECTRICAL INTERLOCKING |  |  |
|  | Electrical interlocking of all sources and bus couplers, including providing & fixing of UV-Shunt relays, auxiliary contacts, control wiring, MCB's for control wiring, etc. as per requirement complete. |  |  |
|  | 33 KV HT PANELS (Utility Block LICAI Building) |  |  |
|  | INCOMER |  |  |
|  | JVVNL 33KV Power Supply For Connecting 3C x 300 Sqmm Cable VCB HT Panel _ 2 Incoming |  |  |
|  | OUTGOING |  |  |
|  | 1250 A, 33Kv TP VCB _ NDS-HT Supply |  |  |
|  | 1250 A, 33KV, TO VCB Bus Coupler For Changeover |  |  |
|  | 1250 A, 33Kv TP VCB _ DS-HT Supply |  |  |
|  | Suitable space for cable gland for 4 nos. X 3 C x 300 sq. mm. at O/G |  |  |
| 2 | Supply, Installation, testing and commissioning of 33 KV 4 pole structure ( For Double Break Horizontal 33 KV Isolator with MS Lattice tower including necessary channel support, angle frame, hardware ( nuts, bolts etc ). The work should be complete in all respect including digging of pit for pole structure, concrete filling etc. ( Supply, Installation, testing and commissioning of 33 KV 4 pole structure ( For Double Break Horizontal 33 KV Isolator with MS Lattice tower including necessary channel support, angle frame, hardware ( nuts, bolts etc ). The work should be complete in all respect including digging of pit for pole structure, concrete filling etc. ( Isolator and insulator is not the part of this items ). The MS structure shall have two coat of red oxide, one coat of sliver paint for protecting from rust.Supply, Installation, testing and commissioning of 33 KV, 1250 AMP, Double break horizontal isolator having connecting pipes, clamps support, GO switch, dropout fuse, DO arrangement having insulators, operating pipe rod for GO switch. necessary jumper wire connection. Supply, Installation, testing and commissioning of 33 KV, 1250 AMP, Lighting arrester substation type, 30 KV, 10KA with surge counter. Supply, Installation, testing and commissioning of 33 KV HT meter cubical panel with proper cable gland opening from side or bottom entry, provision of TTB and HT meter fixing arrangement, front opening door, The meter panel shall be made of recommended gauge , colour, powder coated With 33 KV Metering TTB ( As per JVVNL norms) " Isolator and insulator is not the part of this items ). The MS structure shall have two coat of red oxide, one coat of sliver paint for protecting from rust. (As per JVVNL norms) | 1 | Set |
|  | 33 KV Metering (As Per JVVNL Normas) _ 33KV DS- HT Meter_ 1 Nos. (Utility Block LICAI Building) |  |  |
| 3 | SITC of Indoor Type Floor mounted metal clad 33 KV,1250 Amps 3 phase, 50 Hz Vacuum Circuit Breaker (VCB) as per IEC 62271-1,100,200, IS- 13118 Standard made from Powder painted pre-fabricated, CRCA sheet steel /High quality Aluminium-Zinc (Aluzinc) coated sheet steel. Fabrication shall be done through CNC turret press and CNC bending machine having a rupturing capacity of 500 MVA, 26.3 KA breaking capacity for 3 sec, Internal arc type tested for 26.3KA for 1 sec with AFLR clasification totally enclosed with Copper bus bar of 1250 Amps for each phase, flush front, Horizontal isolation, Horizontal drawout type with Electrical and Mechanical interlock and automatic safety shutter gear including padlocking arrangement, isolation plugs, assambly of 4 vaccum interrupters , with each pole individually encapsulated by epoxy insulations to make it dust proof and self - aligning finger type isolating contacts, truck having integral racking with necessary interlocks (for insertion and removing of VCB), manual and automatic motor charged independent closing/ tripping spring , trip free operating mechanism with closing and tripping push buttons and mechanical breaker.Interconnected with HT sleeve bus bar of 1250 Amps , Basic Insulation level (BIL) : 36KV (RMS) / 170KV (Peak) and Altiude less than 1000 meters, including all protection, indication, Operation, monitoring and control and accessories etc. as required. .Factory Tests of VCB panel as per OEM's QAP in it's own Manufacturing facility shall be witnessed by department Engineer virtually / Physically. All as per pre approved by Engineer in charge."1 Incoming 1 Outgoing Panel comprising of Side cable box & Transformer Auxiliary protection and comprising of following. MAKE: SEIMENS/ABB/SCHNEIDER - VCB 1250 Amps . VI of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : 400-200A/ 1-1 A, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA (How ever CT Ratio shall be decided as per load requirement) - VT Ratio: 33KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selectorswitch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. " | 1 | Nos |
|  | 33 KV HT PANELS (Utility Block LICAI Building) |  |  |
|  | INCOMER |  |  |
|  | DS - HT Meter Outgoing _ VCB HT Panel _ 1 Incoming |  |  |
|  | OUTGOING |  |  |
|  | 1250 A, 33Kv TP VCB _DS-HT Supply Feed to 33 Kv/11KV Transformer _ 1 Outgoing ( EXTENSIBLE ) |  |  |
| 4 | SITC of Indoor Type Floor mounted metal clad 33 KV,1250 Amps 3 phase, 50 Hz Vacuum Circuit Breaker (VCB) as per IEC 62271-1,100,200, IS- 13118 Standard made from Powder painted pre-fabricated, CRCA sheet steel /High quality Aluminium-Zinc (Aluzinc) coated sheet steel. Fabrication shall be done through CNC turret press and CNC bending machine having a rupturing capacity of 500 MVA, 26.3 KA breaking capacity for 3 sec, Internal arc type tested for 26.3KA for 1 sec with AFLR clasification totally enclosed with Copper bus bar of 1250 Amps for each phase, flush front, Horizontal isolation, Horizontal drawout type with Electrical and Mechanical interlock and automatic safety shutter gear including padlocking arrangement, isolation plugs, assambly of 4 vaccum interrupters , with each pole individually encapsulated by epoxy insulations to make it dust proof and self - aligning finger type isolating contacts, truck having integral racking with necessary interlocks (for insertion and removing of VCB), manual and automatic motor charged independent closing/ tripping spring , trip free operating mechanism with closing and tripping push buttons and mechanical breaker.Interconnected with HT sleeve bus bar of 1250 Amps , Basic Insulation level (BIL) : 36KV (RMS) / 170KV (Peak) and Altiude less than 1000 meters, including all protection, indication, Operation, monitoring and control and accessories etc. as required. .Factory Tests of VCB panel as per OEM's QAP in it's own Manufacturing facility shall be witnessed by department Engineer virtually / Physically. All as per pre approved by Engineer in charge."1 Incoming & 1 Outgoing Panel comprising of Side cable box & Transformer Auxiliary protection and comprising of following. MAKE: SEIMENS/ABB/SCHNEIDER - VCB 1250 Amps . VI of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : 400-200A/ 1-1 A, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA (How ever CT Ratio shall be decided as per load requirement) - VT Ratio: 33KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selectorswitch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. " | 1 | Nos |
|  | 33 KV NDS _ HT PANELS ( At 11 KV Substation Exting ) |  |  |
|  | INCOMER |  |  |
|  | NDS - HT Meter Outgoing _ VCB HT Panel _ 1 Incoming |  |  |
|  | OUTGOING |  |  |
|  | 1250A, 33Kv TP VCB _NDS-HT Supply Feed to 33 Kv/0.433 KV Transformer 1 Outgoing (EXTENSIBLE ) |  |  |
| 5 | SITC of Indoor Type Floor mounted metal clad 33 KV,1250 Amps 3 phase, 50 Hz Vacuum Circuit Breaker (VCB) as per IEC 62271-1,100,200, IS- 13118 Standard made from Powder painted pre-fabricated, CRCA sheet steel /High quality Aluminium-Zinc (Aluzinc) coated sheet steel. Fabrication shall be done through CNC turret press and CNC bending machine having a rupturing capacity of 500 MVA, 26.3 KA breaking capacity for 3 sec, Internal arc type tested for 26.3KA for 1 sec with AFLR clasification totally enclosed with Copper bus bar of 1250 Amps for each phase, flush front, Horizontal isolation, Horizontal drawout type with Electrical and Mechanical interlock and automatic safety shutter gear including padlocking arrangement, isolation plugs, assambly of 4 vaccum interrupters , with each pole individually encapsulated by epoxy insulations to make it dust proof and self - aligning finger type isolating contacts, truck having integral racking with necessary interlocks (for insertion and removing of VCB), manual and automatic motor charged independent closing/ tripping spring , trip free operating mechanism with closing and tripping push buttons and mechanical breaker.Interconnected with HT sleeve bus bar of 1250 Amps , Basic Insulation level (BIL) : 36KV (RMS) / 170KV (Peak) and Altiude less than 1000 meters, including all protection, indication, Operation, monitoring and control and accessories etc. as required. .Factory Tests of VCB panel as per OEM's QAP in it's own Manufacturing facility shall be witnessed by department Engineer virtually / Physically. All as per pre approved by Engineer in charge."1 Incoming 2 Outgoing Panel comprising of Side cable box & Transformer Auxiliary protection and comprising of following. MAKE: SEIMENS/ABB/SCHNEIDER - VCB 1250 Amps . VI of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : 400-200A/ 1-1 A, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA (How ever CT Ratio shall be decided as per load requirement) - VT Ratio: 33KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selectorswitch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. " | 1 | Nos |
|  | 33 KV HT PANELS |  |  |
|  | INCOMER (Utility Block LICAI Building) |  |  |
|  | 1250A,VCB TP 33KV Power Supply For NDS - HT Connection _ 3x 300Sqmm 33KV Cable (Meter Outgoing Connected In Panel ) |  |  |
|  | OUTGOING |  |  |
|  | 1250 A, 33Kv TP VCB _ NDS-HT Supply _ For LICAI |  |  |
|  | 800 A, 33Kv TP VCB _ NDS-HT Supply _ For Existing 11 Kv Power Supply Feed |  |  |
|  | Suitable space for cable gland for 4 nos. X 3 C x 300/185 sq. mm. at O/G |  |  |
| 6 | Supply installation testing & Commissioning of 11 KV Indoor, 1no. Incomer , 3 no. outgoing Vacuum Circuit Breaker Panel Comprising of 11kV, 26.3kA/1-sec, Draw-Out type HT Vacuum Circuit breaker panel confirming to IEC 62271-200, IAC AFLR – 26.3kA for 1sec, LSC2B-PM Class, comprising of 800Amp, continuous rated Alum busbars and droppers with Standard Specs With SCADA System with Metering Instruments: Multifunction Meter with RS485 port for MODBUS communication (Acc.Cl.0.5), Digital Ammeter (Acc.Cl.0.5), Digital Voltmeter (Acc.Cl.0.5) with PT Drawout type and as per Standards . MAKE: SEIMENS/ABB/SCHNEIDER | 1 | Nos |
|  | 11 KV DS - HT PANELS _ (Utility Block LICAI Building) |  |  |
|  | INCOMER |  |  |
|  | 1250A,11KV Power Supply For DS - HT Connection _ 3x 300Sqmm 11KV Cable Connected 5MVA 33KV/11 KV Transformer |  |  |
|  | OUTGOING |  |  |
|  | 800 A, 11Kv TP VCB _ DS-HT Supply _ Connected _ Existing 11KV ,3C x 185sqmm cable _ 11 KV Substation Existing feed Power Supply _1 |  |  |
|  | 800 A, 11Kv TP VCB _ DS-HT Supply _ Connected _ Existing 11KV ,3C x 185 sqmm cable _ 11 KV Substation Existing feed Power Supply _2 |  |  |
|  | 800 A, 11Kv TP VCB _ DS-HT Supply _ Connected _ Existing 11KV ,3C x 185 sqmm cable _ 11 KV Substation Existing feed Power Supply _3 (Future Provision VRV AC In Hostels) |  |  |
|  | Suitable space for cable gland for 4 nos. X 3 C x 185 sq. mm. at O/G |  |  |
|  | ELECTRICAL INTERLOCKING |  |  |
|  | Electrical interlocking of all sources and bus couplers, including providing & fixing of UV-Shunt relays, auxiliary contacts, control wiring, MCB's for control wiring, etc. as per requirement complete. |  |  |
| 7 | Supply installation testing & Commissioning of Copper wound distribution Transformer of following rating and % Impedance, 33 / 11KV 5 MVA Power ONAN Cooled losses as per IS 1180 part I 2014 (Fourth Revision) Level-II, with boltless core design including standard accessories like conservator with prismatic oil level gauge , silica gel breather, Bucholz relay, pressed steel radiator fins, Radiator Valve Suitable size HT cable box, LT cable box with Busbar connection for outgoing cables, Off -LTC (+/- 2.5%, +/- 5% to - 7.5% ), temperature rise of 40 degree C in oil / 45 degree C in winding , drain valve, Air release device, Dial type Oil & Winding Temperature gauge with alarm & trip contacts, first filling of transformer oil as per IS :335-1953 , Epoxy primer and PU based paint as Top coat, The Transformer shall be subjected to routine factory tests (as per IS:2026 and IS:1180) including Temperature rise test in OEM's own lab shall be witnessed by Engineer Physically. Transformer shall be tested from CTL of discom before charging of transformer & complete installaion must be certified from Electrical Inspectorate office as per Indian Electricity rule, (CTL testing charges and Electrical Inspection charges shall be reimbursed by the department to the contractor)Following tests shall be carried out on each transformer at site by OEM enginer in presence of department authorised representative:- a) Ratio test on each tapping.b) Resistance of windings at principal and all tapings.c) Insulation resistance of the winding between HV to earth / HV to LV / LV to earth.d) Vector group test.e) Magnetic Balance test. All as per pre approved by Engineer in charge. 5000 KVA with % Impedance 6.25 . MAKE: CROMTPON GREVES/ABB/VOLTAMP | 1 | Nos |
| 8 | Supply, Laying, termination, testing and commissioning of 33 KV grade Dry cure, 3C x 185 sqmm 33kv HT XLPE cable with the help of Vernier Machine (Trench Less Machine) as per relevent IS Standard Practice of same The Cable shall be approved by JVVNL & Passed by CTL ( 11 Kv Substation to Gate No. 2 to Gate No. 3 to Utility Block_ 700+320+150 = 1170 meter ) | 1170 | R.Mtrs |
| 9 | Supply, Laying, termination, testing and commissioning of 33 KV grade Dry cure, 3C x 300 sqmm 33kv HT XLPE cable with as per relevent IS Standard Practice of same The Cable shall be approved by JVVNL & Passed by CTL | 100 | R.Mtrs |
| 10 | Supply, Laying, termination, testing and commissioning of 11 KV grade Dry cure, 3C x 185 sqmm 11kv HT XLPE cable with the help of Vernier Machine (Trench Less Machine) as per relevent IS Standard Practice of same The Cable shall be approved by JVVNL & Passed by CTL ( Gate No. 2 to Gate No. 3 to Utility Block _ 3 nos. x 620 (300+320=620) = 1860+50=1910 meter ) | 1910 | R.Mtrs |
| 11 | Supply, Laying, termination, testing and commissioning of 11 KV grade Dry cure, 3.5C x 300 sqmm LT XLPE cable ,as per relevent IS Standard Practice of same The Cable shall be approved by JVVNL & Passed by CTL (1600KVA Transformer to LT VCB Panel _ 100 100 meter For 11 KV Substation NDS - HT | 100 | R.Mtrs |
| 12 | Supply, erection, testing and commissioning of earthing with Cu plate earthing 600mm x 600mm x 3mm including accessories and providing brick masonary chamber with neat cement finish enclosure with CI cover plate having locking arrangement with funnel & watering pipe complete with charcoal and salt etc. as required as per technical specifications and IS: 3043 compete as required. The earth resistance shall be checked and should be less then 1 ohm. | 6 | Nos |
| 13 | Supply, erection, testing and commissioning of earthing with GI plate earthing 600mm x 600mm x 6mm including accessories and providing brick masonary chamber with neat cement finish enclosure with CI cover plate having locking arrangement with funnel & watering pipe complete with charcoal and salt etc. as required as per technical specifications and IS: 3043 compete as required. The earth resistance shall be checked and should be less then 1 ohm. | 16 | Nos |
| 14 | Providing and fixing of 50x6mm G.I. Strip on surface or in recess for connections etc. as required. | 100 | R.Mtrs |
| 15 | Providing and fixing of 50x6mm Copper Strip on surface or in recess for connections etc. as required. | 100 | R.Mtrs |
| 16 | Supply & fixing of End cable jointing termination Kit suitable for 3.5Cx300sqmm, LT XLPE (E) grade armoured cable (Raychem, 3M, Seal) (3.5c x300Sqmm LT Cable Termination Removing _ 18 Nos. ) 18 Nos. | 18 | Nos. |
| 17 | Supply & fixing of Heat shrink indoor cable jointing termination Kit suitable for 3Cx185sqmm, 33kv/11KV HT XLPE (E) grade armoured cable (Raychem, 3M, Seal) | 16 | Nos |
| 18 | Supply & fixing of Heat shrink outdoor cable jointing termination Kit suitable for 3Cx185sqmm, 33kv/11KV HT XLPE (E) grade armoured cable (Raychem, 3M, Seal) | 16 | Nos |
| 19 | Supply & fixing of Heat shrink Straight through joint cable termination Kit suitable for 3Cx300sqmm 33 Kv XLPE (E) grade armoured cable (Raychem, Cabseal, 3M, Seal) | 2 | Nos |
| 20 | Supply & fixing of Heat shrink Straight through joint cable termination Kit suitable for 3Cx 185 sqmm 33Kv XLPE (E) grade armoured cable (Raychem, Cabseal, 3M, Seal) | 2 | Nos |
| 21 | Supply & fixing of Heat shrink Straight through joint cable termination Kit suitable for 3Cx 185 sqmm 11Kv XLPE (E) grade armoured cable (Raychem, Cabseal, 3M, Seal) | 8 | Nos |
| 22 | Supply installation testing & Commissioning of Copper wound distribution Transformer of following rating and % Impedance, 11 / 0.433KV 1600 KVA Delta-Star Connected, Vector Group Dyn 11, ONAN Cooled losses as per IS 1180 part I 2014 (Fourth Revision) Level-II, with boltless core design including standard accessories like conservator with prismatic oil level gauge , silica gel breather, Bucholz relay, pressed steel radiator fins, Radiator Valve(above 1600 Kva) Suitable size HT cable box, LT cable box with Busbar connection for outgoing cables, Off -LTC (+/- 2.5%, +/- 5% to - 7.5% ), temperature rise of 40 degree C in oil / 45 degree C in winding , drain valve, Air release device, Dial type Oil & Winding Temperature gauge with alarm & trip contacts, first filling of transformer oil as per IS :335-1953 , Epoxy primer and PU based paint as Top coat, Unidirectional rollers for rating upto 800 kva & bi- directionalabove 800 Kva rollers with locking arrangement etc. as required. The Transformer shall be subjected to routine factory tests (as per IS:2026 and IS:1180) including Temperature rise test in OEM’s own lab shall be witnessed by Engineer Physically. Transformer shall be tested from CTL of discom before charging of transformer & complete installation must be certified from Electrical Inspectorate office as per Indian Electricity rule, (CTL testing charges and Electrical Inspection charges shall be reimbursed by the department to the contractor)Following tests shall be carried out on each transformer at site by OEM engineer in presence of department authorised representative:- a) Ratio test on each tapping.b) Resistance of windings at principal and all tapings.c) Insulation resistance of the winding between HV to earth / HV to LV / LV to earth.d) Vector group test.e) Magnetic Balance test. All as per pre-approved by Engineer in charge. MAKE: CROMTPON GREVES/ABB/VOLTAMP | 1 | Nos |
| 23 | Supply and laying of 32 mm insulated rubber mat inside the HT meter cubical room. The size of rubber mat shall be 2mtrs x 1mtrs. Vendor shall share sample with Client prior placing the order. | 10 | R.Mtrs |
| 24 | Civil work Civil work (Labour + Material) Foundation of Transformer, MS angle as per Required & AND OTHER MISCELLANEOUS CHARGES | 1 | Job |
| 25 | Approval for Electrical Inspector & JVVNL |  |  |
| a. | Electrical Inspector fee consultancy and other charges | 1 | Job |
| b. | Charges for obtaining approval/NOC from the office of Electrical Inspector, Jaipur, (other than the fee levied by the Electrical Inspector's Office) for the HT electrical installations. Fees levied by the Office of Electrical Inspector will be reimbursed by the Institute on presentation of actual receipts / paid by the institute on receiving demand notice from the office. | 1 | Job |

Annexure-1

AFFIDAVIT

- I, the undersigned, do hereby certify that all the statements made in the required statements are true & correct.

- The undersigned also hereby certifies that neither our firms M/s___________________ have abandoned any work in previous projects or in any other Department nor any contract awarded to us for such works have been rescinded, during last five years prior to the date of this bid.

- The undersigned understand and agrees that further qualifying information may be requested and agrees to furnish any such information at the request of M/s Laxmi Niwas Mittal Institute of Information Technology LNMIIT, Jaipur.

………………………………………………………..

(Signed by an Authorized Person of Firm)

………………………………………………

(Title of the Authorized Person)

…………………………………………….

(Name of Firm )

On non-judicial stamp paper of minimum Rs. 100/-)

Form of Bank Guarantee for Earnest Money Deposit /                     Performance Guarantee / Security Deposit

To

M/s LNM Institute of Information Technology,

Gram: Rupa ki Nangal,Post: Sumel

Jaipur-302031, Rajasthan.

- In consideration of M/s LNM Institute of Information Technology ( LNMIIT) – jointly established in 2002 by the state government of Rajasthan and the Lakshmi & Usha Mittal foundation, having its registered office at Gram: Rupa Ki Nangal, Post Sumel, Via Jamdoli, Jaipur, Rajasthan ( India ) – 302031  (hereinafter called “the Company” (which expression shall include its successor in business and assignees) have agreed to accept irrevocable bank guarantee of Rs……………………….( rupees………………….only ) valid upto……… (date) as Earnest Money Deposit from…………………( name and address of the “contractor”) for compliance of his obligations in accordance with the terms and conditions of the said NIT.

OR

In consideration of M/s LNM  Institute of Information Technology     ( LNMIIT ) – jointly established in 2002 by the state government of Rajasthan and the Lakshmi & Usha Mittal foundation, having its registered office at Gram: Rupa Ki Nangal, Post Sumel, Via Jamdoli, Jaipur, Rajasthan ( India ) – 302031  (hereinafter called “the Company” (which expression shall include its successor in business and assignees) have agreed to accept irrevocable bank guarantee of Rs……………………….( rupees………………….only ) valid upto……… (date) as Performance Guarantee/Security Deposit/Mobilisation Advance from the said contractor for compliance of his obligations in accordance with the terms and conditions of the agreement.

- We, ................ (Indicate the name of the bank) ..........................., (herein after referred to as “the Bank”), hereby undertake to pay to the COMPANY an amount not exceeding Rs ................................ (Rupees.............................................. only) on demand by the COMPANY within 10 days of the demand.

- We, ......................... (Indicate the name of the Bank) ................, do here by undertake to pay the amount due and payable under this guarantee without any demur, merely on a demand from the Government stating that the amount claimed is required to meet the recoveries due or likely to be due from the said Contractor. Any such demand made on the Bank shall be conclusive as regards the amount due and payable by the Bank under this Guarantee. However, our liability under this guarantee shall be restricted to an amount not exceeding Rs................... (Rupees ........................ only)

- We, .......................................(indicate the name of the Bank) ..................., further undertake to pay the Company any money so demanded notwithstanding any dispute or disputes raised by the contractor in any suit or proceeding pending before any Court or Tribunal, our liability under this Bank Guarantee being absolute and unequivocal. The payment so made by us under this Bank Guarantee shall be a valid discharge of our liability for payment there under and the Contractor shall have no claim against us for making such payment.

- We, ....................................(indicate the name of the Bank..............................., further agree that the Company shall have the fullest liberty without our consent and without affecting in any manner our obligation here under to vary any of the terms and conditions of the said agreement or to extend time of performance by the said Contractor from time to time or to postpone for any time or from time to time any of the powers exercisable by the Company against the said contractor and to forbear or enforce any of the terms and conditions relating to the said agreement and we shall not be relieved from our liability by reason of any such variation or extension being granted to the said Contractor or for any forbearance, act of omission on the part of the Company or any indulgence by the Company to the said Contractor or by any such matter or thing whatsoever which under the law relating to sureties would, but for this provision, have effect of so relieving us.

- We, ...................(indicate the name of the Bank) ........................................................ further agree that the Company at its option shall be entitled to enforce this guarantee against the Bank as a principal debtor at the first instance without proceeding against the Contractor and notwithstanding any security or other guarantee the Company may have in relation to the Contractor's liabilities.

- This guarantee will not be discharged due to the change in the constitution of the Bank or the Contractor.

- We, .......................................(Indicate the name of the Bank) ...................undertake not to revoke this guarantee except with the consent of the Company in writing.

- This Bank Guarantee shall be valid up to ...................................................... unless extended on demand by the Government. Notwithstanding anything mentioned above, our liability against this guarantee is restricted to Rs......................... (Rupees............................................................only) and unless a claim in writing is lodged with us within the date of expiry or extended date of expiry of this guarantee, all our liabilities under this guarantee shall stand discharged.

Date :…………….

Witnesses:

- Signature……….

Name and Address					Authorised signatory

Name ……….

Designation……..

Staff code No…….

Bank seal………..

- Signature……….

Name and Address

- In paragraph 1, strike out the portion not applicable. Bank Guarantee will be made either for earnest money or for performance guarantee/security deposit/mobilization advance, as the case may be.

Price Bid

(To be submitted separately in a sealed Envelope on company’s letter head)

Name of the Project: Supply, Installation, Testing and Commissioning of External Electrical HT Panels, Cabling and Transformer Work for JVVNL DS – HT Metering & Indoor Distribution 33 kV System

UPGRADATION WORK: 11 kV → 33 kV SUBSTATION _ External Electrical Works HT Panel, Cable and Transformer

| S.No. | Item Description | Qty | Unit | Rate | Amount |
| --- | --- | --- | --- | --- | --- |
| 1 | SITC of Indoor Type Floor mounted metal clad 33 KV,1250 Amps 3 phase, 50 Hz Vacuum Circuit Breaker (VCB) as per IEC 62271-1,100,200, IS- 13118 Standard made from Powder painted prefabricated, CRCA sheet steel /High quality Aluminium-Zinc (Aluzinc) coated sheet steel. Fabrication shall be done through CNC turret press and CNC bending machine having a rupturing capacity of 500 MVA, 26.3 KA breaking capacity for 3 sec, Internal arc type tested for 26.3KA for 1 sec with AFLR classification totally enclosed with Copper bus bar of 1250 Amps for each phase, flush front, Horizontal isolation, Horizontal drawout type with Electrical and Mechanical interlock and automatic safety shutter gear including padlocking arrangement, isolation plugs, assembly of 4 vaccum interrupters , with each pole individually encapsulated by epoxy insulations to make it dust proof and self - aligning finger type isolating contacts, truck having integral racking with necessary interlocks (for insertion and removing of VCB), manual and automatic motor charged independent closing/ tripping spring , trip free operating mechanism with closing and tripping push buttons and mechanical breaker. Interconnected with HT sleeve bus bar of 1250 Amps , Basic Insulation level (BIL) : 36KV (RMS) / 170KV (Peak) and Altiude less than 1000 meters, including all protection, indication, Operation, monitoring and control and accessories etc. as required. . Factory Tests of VCB panel as per OEM's QAP in it's own Manufacturing facility shall be witnessed by department Engineer virtually / Physically. All as per pre approved by Engineer in charge."2 Incoming 2 Outgoing One Bus Coupler Panel comprising of Side cable box & Transformer Auxiliary protection and comprising of following. MAKE: SEIMENS/ABB/SCHNEIDER | 1 | Nos | RO |  |
|  | VCB 1250 Amps . VI of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continuous rating to achive minimal failure. - Resin Cast type CT having Ratio : 400-200A/ 1-1 A, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA (How ever CT Ratio shall be decided as per load requirement) - VT Ratio: 33KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selectorswitch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. " |  |  |  |  |
|  | ELECTRICAL INTERLOCKING |  |  |  |  |
|  | Electrical interlocking of all sources and bus couplers, including providing & fixing of UV-Shunt relays, auxiliary contacts, control wiring, MCB's for control wiring, etc. as per requirement complete. |  |  |  |  |
|  | 33 KV HT PANELS (Utility Block LICAI Building) |  |  |  |  |
|  | INCOMER |  |  |  |  |
|  | JVVNL 33KV Power Supply For Connecting 3C x 300 Sqmm Cable VCB HT Panel _ 2 Incoming |  |  |  |  |
|  | OUTGOING |  |  |  |  |
|  | 1250 A, 33Kv TP VCB _ NDS-HT Supply |  |  |  |  |
|  | 1250 A, 33KV, TO VCB Bus Coupler For Changeover |  |  |  |  |
|  | 1250 A, 33Kv TP VCB _ DS-HT Supply |  |  |  |  |
|  | Suitable space for cable gland for 4 nos. X 3 C x 300 sq. mm. at O/G |  |  |  |  |
| 2 | Supply, Installation, testing and commissioning of 33 KV 4 pole structure (For Double Break Horizontal 33 KV Isolator with MS Lattice tower including necessary channel support, angle frame, hardware (nuts, bolts etc). The work should be complete in all respect including digging of pit for pole structure, concrete filling etc. (Supply, Installation, testing and commissioning of 33 KV 4 pole structure (For Double Break Horizontal 33 KV Isolator with MS Lattice tower including necessary channel support, angle frame, hardware (nuts, bolts etc ). The work should be complete in all respect including digging of pit for pole structure, concrete filling etc. (Isolator and insulator is not the part of this items). The MS structure shall have two coats of red oxide, one coat of sliver paint for protecting from rust. Supply, Installation, testing and commissioning of 33 KV, 1250 AMP, Double break horizontal isolator having connecting pipes, clamps support, GO switch, dropout fuse, DO arrangement having insulators, operating pipe rod for GO switch. necessary jumper wire connection. Supply, Installation, testing and commissioning of 33 KV, 1250 AMP, Lighting arrester sub station type, 30 KV, 10KA with surge counter. Supply, Installation, testing and commissioning of 33 KV HT meter cubical panel with proper cable gland opening from side or bottom entry, provision of TTB and HT meter fixing arrangement, front opening door, The meter panel shall be made of recommended gauge , colour, powder coated With 33 KV Metering TTB ( As per JVVNL norms) " Isolator and insulator is not the part of this items ). The MS structure shall have two coat of red oxide, one coat of sliver paint for protecting from rust. (As per JVVNL norms) | 1 | Set |  |  |
|  | 33 KV Metering (As Per JVVNL Normas) _ 33KV DS- HT Meter_ 1 Nos. (Utility Block LICAI Building) |  |  |  |  |
| 3 | SITC of Indoor Type Floor mounted metal clad 33 KV,1250 Amps 3 phase, 50 Hz Vacuum Circuit Breaker (VCB) as per IEC 62271-1,100,200, IS- 13118 Standard made from Powder painted pre-fabricated, CRCA sheet steel /High quality Aluminium-Zinc (Aluzinc) coated sheet steel. Fabrication shall be done through CNC turret press and CNC bending machine having a rupturing capacity of 500 MVA, 26.3 KA breaking capacity for 3 sec, Internal arc type tested for 26.3KA for 1 sec with AFLR clasification totally enclosed with Copper bus bar of 1250 Amps for each phase, flush front, Horizontal isolation, Horizontal drawout type with Electrical and Mechanical interlock and automatic safety shutter gear including padlocking arrangement, isolation plugs, assambly of 4 vaccum interrupters , with each pole individually encapsulated by epoxy insulations to make it dust proof and self - aligning finger type isolating contacts, truck having integral racking with necessary interlocks (for insertion and removing of VCB), manual and automatic motor charged independent closing/ tripping spring , trip free operating mechanism with closing and tripping push buttons and mechanical breaker.Interconnected with HT sleeve bus bar of 1250 Amps , Basic Insulation level (BIL) : 36KV (RMS) / 170KV (Peak) and Altiude less than 1000 meters, including all protection, indication, Operation, monitoring and control and accessories etc. as required. .Factory Tests of VCB panel as per OEM's QAP in it's own Manufacturing facility shall be witnessed by department Engineer virtually / Physically. All as per pre approved by Engineer in charge."1 Incoming 1 Outgoing Panel comprising of Side cable box & Transformer Auxiliary protection and comprising of following. MAKE: SEIMENS/ABB/SCHNEIDER - VCB 1250 Amps . VI of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : 400-200A/ 1-1 A, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA (How ever CT Ratio shall be decided as per load requirement) - VT Ratio: 33KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selectorswitch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. " | 1 | Nos | RO |  |
|  | 33 KV HT PANELS (Utility Block LICAI Building) |  |  |  |  |
|  | INCOMER |  |  |  |  |
|  | DS - HT Meter Outgoing _ VCB HT Panel _ 1 Incoming |  |  |  |  |
|  | OUTGOING |  |  |  |  |
|  | 1250 A, 33Kv TP VCB _DS-HT Supply Feed to 33 Kv/11KV Transformer _ 1 Outgoing ( EXTENSIBLE ) |  |  |  |  |
| 4 | SITC of Indoor Type Floor mounted metal clad 33 KV,1250 Amps 3 phase, 50 Hz Vacuum Circuit Breaker (VCB) as per IEC 62271-1,100,200, IS- 13118 Standard made from Powder painted pre-fabricated, CRCA sheet steel /High quality Aluminium-Zinc (Aluzinc) coated sheet steel. Fabrication shall be done through CNC turret press and CNC bending machine having a rupturing capacity of 500 MVA, 26.3 KA breaking capacity for 3 sec, Internal arc type tested for 26.3KA for 1 sec with AFLR clasification totally enclosed with Copper bus bar of 1250 Amps for each phase, flush front, Horizontal isolation, Horizontal drawout type with Electrical and Mechanical interlock and automatic safety shutter gear including padlocking arrangement, isolation plugs, assembly of 4 vaccum interrupters , with each pole individually encapsulated by epoxy insulations to make it dust proof and self - aligning finger type isolating contacts, truck having integral racking with necessary interlocks (for insertion and removing of VCB), manual and automatic motor charged independent closing/ tripping spring , trip free operating mechanism with closing and tripping push buttons and mechanical breaker. Interconnected with HT sleeve bus bar of 800 Amps , Basic Insulation level (BIL) : 36KV (RMS) / 170KV (Peak) and Altiude less than 1000 meters, including all protection, indication, Operation, monitoring and control and accessories etc. as required. . Factory Tests of VCB panel as per OEM's QAP in it's own Manufacturing facility shall be witnessed by department Engineer virtually / Physically. All as per pre approved by Engineer in charge."1 Incoming & 1 Outgoing Panel comprising of Side cable box & Transformer Auxiliary protection and comprising of following. MAKE: SEIMENS/ABB/SCHNEIDER - VCB 1250 Amps. VI of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : 400-200A/ 1-1 A, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA (How ever CT Ratio shall be decided as per load requirement) - VT Ratio: 33KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selector switch and Volt meter with Selector switch - Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. " | 1 | Nos |  |  |
|  | 33 KV NDS _ HT PANELS ( At 11 KV Substation Exiting ) |  |  |  |  |
|  | INCOMER |  |  |  |  |
|  | NDS - HT Meter Outgoing _ VCB HT Panel _ 1 Incoming |  |  |  |  |
|  | OUTGOING |  |  |  |  |
|  | 1250 A, 33Kv TP VCB _NDS-HT Supply Feed to 33 Kv/0.433 KV Transformer 1 Outgoing ( EXTENSIBLE ) |  |  |  |  |
| 5 | SITC of Indoor Type Floor mounted metal clad 33 KV,1250 Amps 3 phase, 50 Hz Vacuum Circuit Breaker (VCB) as per IEC 62271-1,100,200, IS- 13118 Standard made from Powder painted pre-fabricated, CRCA sheet steel /High quality Aluminium-Zinc (Aluzinc) coated sheet steel. Fabrication shall be done through CNC turret press and CNC bending machine having a rupturing capacity of 500 MVA, 26.3 KA breaking capacity for 3 sec, Internal arc type tested for 26.3KA for 1 sec with AFLR clasification totally enclosed with Copper bus bar of 1250 Amps for each phase, flush front, Horizontal isolation, Horizontal drawout type with Electrical and Mechanical interlock and automatic safety shutter gear including padlocking arrangement, isolation plugs, assambly of 4 vaccum interrupters , with each pole individually encapsulated by epoxy insulations to make it dust proof and self - aligning finger type isolating contacts, truck having integral racking with necessary interlocks (for insertion and removing of VCB), manual and automatic motor charged independent closing/ tripping spring , trip free operating mechanism with closing and tripping push buttons and mechanical breaker.Interconnected with HT sleeve bus bar of 1250 Amps , Basic Insulation level (BIL) : 36KV (RMS) / 170KV (Peak) and Altiude less than 1000 meters, including all protection, indication, Operation, monitoring and control and accessories etc. as required. .Factory Tests of VCB panel as per OEM's QAP in it's own Manufacturing facility shall be witnessed by department Engineer virtually / Physically. All as per pre approved by Engineer in charge."1 Incoming 2 Outgoing Panel comprising of Side cable box & Transformer Auxiliary protection and comprising of following. MAKE: SEIMENS/ABB/SCHNEIDER - VCB 1250 Amps . VI of VCB should be sealed for 30000 operation. VCB operationg mechanism should be of M2 duty for minimum 10000 mechanical operation. - Closing & tripping coil of VCB should be of continious rating to achive minimal failure. - Resin Cast type CT having Ratio : 400-200A/ 1-1 A, Core1: 5P20, 5 VA; Core 2: 0.5, 5 VA (How ever CT Ratio shall be decided as per load requirement) - VT Ratio: 33KV/1.732/110V/1.732/110V/1.732, -Core 1: 0.5, 20VA should be floor mounted and to be connected from the back side of the panel. - Numerical relay (should be VCB manufacturer's own make) having protections of 50,51, 50N,51N,TCS. The relay shall have programable 4 digital Input , programable 6 Digital Output and programable 4 nos. LED at HMI. - Ammeter with Selector switch and Voltmeter with Selector switch | 1 | Nos | RO |  |
|  | Multifunction Meter of Acc Class 0.5, having facility to monitor KW, KVA, KVAR, PF, KWH, KVARH, KVAH, A,V etc. - Trip circuit supervision relay (feature of numerical relay) - LR, TNC switch, indication lamp - CB ON/OFF, spring charge, Auto trip, TCS healthy etc., Space heaters - Power Pack (230V AC- 110V DC) and 8/12 window Annunciator. " |  |  |  |  |
|  | 33 KV HT PANELS |  |  |  |  |
|  | INCOMER (Utility Block LICAI Building) |  |  |  |  |
|  | 1250A, VCB TP 33KV Power Supply for NDS - HT Connection _ 3x 300/185 Sqmm 33KV Cable ( Meter Outgoing Connected In Panel ) |  |  |  |  |
|  | OUTGOING |  |  |  |  |
|  | 1250 A, 33Kv TP VCB _ NDS-HT Supply _ For LICAI |  |  |  |  |
|  | 1250A, 33Kv TP VCB _ NDS-HT Supply _ For Existing 11 Kv Power Supply Feed |  |  |  |  |
|  | Suitable space for cable gland for 4 nos. X 3 C x 300/185 sq. mm. at O/G |  |  |  |  |
| 6 | Supply installation testing & Commissioning of 11 KV Indoor, 1no. Incomer , 3 no. outgoing Vacuum Circuit Breaker Panel Comprising of 11kV, 26.3kA/1-sec, Draw-Out type HT Vacuum Circuit breaker panel confirming to IEC 62271-200, IAC AFLR – 26.3kA for 1sec, LSC2B-PM Class, comprising of 800Amp, continuous rated Alum busbars and droppers with Standard Specs With SCADA System with Metering Instruments: Multifunction Meter with RS485 port for MODBUS communication (Acc.Cl.0.5), Digital Ammeter (Acc.Cl.0.5), Digital Voltmeter (Acc.Cl.0.5) with PT Drawout type and as per Standards . MAKE: SEIMENS/ABB/SCHNEIDER | 1 | Nos |  |  |
|  | 11 KV DS - HT PANELS _ (Utility Block LICAI Building) |  |  |  |  |
|  | INCOMER |  |  |  |  |
|  | 1250A,11KV Power Supply For DS - HT Connection _ 3x 300Sqmm 11KV Cable Connected 5MVA 33KV/11 KV Transformer |  |  |  |  |
|  | OUTGOING |  |  |  |  |
|  | 800 A, 11Kv TP VCB _ DS-HT Supply _ Connected _ Existing 11KV ,3C x 185sqmm cable _ 11 KV Substation Existing feed Power Supply _1 |  |  |  |  |
|  | 800 A, 11Kv TP VCB _ DS-HT Supply _ Connected _ Existing 11KV ,3C x 185 sqmm cable _ 11 KV Substation Existing feed Power Supply _2 |  |  |  |  |
|  | 800 A, 11Kv TP VCB _ DS-HT Supply _ Connected _ Existing 11KV ,3C x 185 sqmm cable _ 11 KV Substation Existing feed Power Supply _3 (Futuer Provision VRV AC In Hostels ) |  |  |  |  |
|  | Suitable space for cable gland for 4 nos. X 3 C x 185 sq. mm. at O/G |  |  |  |  |
|  | ELECTRICAL INTERLOCKING |  |  |  |  |
|  | Electrical interlocking of all sources and bus couplers, including providing & fixing of UV-Shunt relays, auxiliary contacts, control wiring, MCB's for control wiring, etc. as per requirement complete. |  |  |  |  |
| 7 | Supply installation testing & Commissioning of Copper wound distribution Transformer of following rating and % Impedance, 33 / 11KV 5 MVA Power ONAN Cooled losses as per IS 1180 part I 2014 (Fourth Revision) Level-II, with boltless core design including standard accessories like conservator with prismatic oil level gauge , silica gel breather, Bucholz relay, pressed steel radiator fins, Radiator Valve Suitable size HT cable box, LT cable box with Busbar connection for outgoing cables, Off -LTC (+/- 2.5%, +/- 5% to - 7.5% ), temperature rise of 40 degree C in oil / 45 degree C in winding , drain valve, Air release device, Dial type Oil & Winding Temperature gauge with alarm & trip contacts, first filling of transformer oil as per IS :335-1953 , Epoxy primer and PU based paint as Top coat, The Transformer shall be subjected to routine factory tests (as per IS:2026 and IS:1180) including Temperature rise test in OEM's own lab shall be witnessed by Engineer Physically. Transformer shall be tested from CTL of discom before charging of transformer & complete installation must be certified from Electrical Inspectorate office as per Indian Electricity rule, (CTL testing charges and Electrical Inspection charges shall be reimbursed by the department to the contractor)Following tests shall be carried out on each transformer at site by OEM enginer in presence of department authorised representative:- a) Ratio test on each tapping.b) Resistance of windings at principal and all tapings.c) Insulation resistance of the winding between HV to earth / HV to LV / LV to earth.d) Vector group test.e) Magnetic Balance test. All as per pre-approved by Engineer in charge. 5000 KVA with % Impedance 6.25 . MAKE: CROMTPON GREVES/ABB/VOLTAMP (Outdoor Type Transformer) | 1 | Nos |  |  |
| 8 | Supply, Laying, termination, testing and commissioning of 33 KV grade Dry cure, 3C x 185 sqmm 33kv HT XLPE cable with the help of Vernier Machine (Trench Less Machine) as per relevant IS Standard Practice of same The Cable shall be approved by JVVNL & Passed by CTL & Make Polycab/Havells ( 11 Kv Substation to Gate No. 2 to Gate No. 3 to Utility Block_ 700+320+150 = 1170 meter ) | 1170 | R.Mtrs |  |  |
| 9 | Supply, Laying, termination, testing and commissioning of 33 KV grade Dry cure, 3C x 300 sqmm 33kv HT XLPE cable with as per relevent IS Standard Practice of same The Cable shall be approved by JVVNL & Passed by CTL | 100 | R.Mtrs |  |  |
| 10 | Supply, Laying, termination, testing and commissioning of 11 KV grade Dry cure, 3C x 185 sqmm 11kv HT XLPE cable with the help of Vernier Machine (Trench Less Machine) as per relevent IS Standard Practice of same The Cable shall be approved by JVVNL & Passed by CTL& Make Polycab/Havells ( ( Gate No. 2 to Gate No. 3 to Utility Block _ 3 nos. x 620 (300+320=620) = 1860+50=1910 meter ) | 1910 | R.Mtrs |  |  |
| 11 | Supply, Laying, termination, testing and commissioning of 11 KV grade Dry cure, 3.5C x 300 sqmm LT XLPE cable ,as per relevent IS Standard (100-meter 3C x 300 Sqmm old cable removing in cable trench at 11 kv substation (1600KVA Transformer to LT VCB Panel _ 100 meter ) For 11 KV Substation NDS - HT | 100 | R.Mtrs |  |  |
| 12 | Supply, erection, testing and commissioning of earthing with Cu plate earthing 600mm x 600mm x 3mm including accessories and providing brick masonary chamber with neat cement finish enclosure with CI cover plate having locking arrangement with funnel & watering pipe complete with charcoal and salt etc. as required as per technical specifications and IS: 3043 compete as required. The earth resistance shall be checked and should be less then 1 ohm. | 6 | Nos |  |  |
| 13 | Supply, erection, testing and commissioning of earthing with GI plate earthing 600mm x 600mm x 6mm including accessories and providing brick masonry chamber with neat cement finish enclosure with CI cover plate having locking arrangement with funnel & watering pipe complete with charcoal and salt etc. as required as per technical specifications and IS: 3043 compete as required. The earth resistance shall be checked and should be less then 1 ohm. | 16 | Nos |  |  |
| 14 | Providing and fixing of 50x6mm G.I. Strip on surface or in recess for connections etc. as required. | 100 | R.Mtrs |  |  |
| 15 | Providing and fixing of 50x6mm Copper Strip on surface or in recess for connections etc. as required. | 100 | R.Mtrs |  |  |
| 16 | Supply & fixing of End cable jointing termination Kit suitable for 3.5Cx300sqmm, LT XLPE (E) grade armoured cable (Raychem, 3M, Seal) (3.5c x300Sqmm LT Cable Termination Removing _ 18 Nos. ) | 18 | Nos. |  |  |
| 17 | Supply & fixing of Heat shrink indoor cable jointing termination Kit suitable for 3Cx300sqmm, 33kv/11KV HT XLPE (E) grade armoured cable (Raychem, 3M, Seal) | 16 | Nos |  |  |
| 18 | Supply & fixing of Heat shrink outdoor cable jointing termination Kit suitable for 3Cx300sqmm, 33kv/11KV HT XLPE (E) grade armoured cable (Raychem, 3M, Seal) | 16 | Nos |  |  |
| 19 | Supply & fixing of Heat shrink Straight through joint cable termination Kit suitable for 3Cx300sqmm 33 Kv XLPE (E) grade armoured cable (Raychem, Cabseal, 3M, Seal) | 2 | Nos |  |  |
| 20 | Supply & fixing of Heat shrink Straight through joint cable termination Kit suitable for 3Cx 185 sqmm 33Kv XLPE (E) grade armoured cable (Raychem, Cabseal, 3M, Seal) | 2 | Nos |  |  |
| 21 | Supply & fixing of Heat shrink Straight through joint cable termination Kit suitable for 3Cx 185 sqmm 11Kv XLPE (E) grade armoured cable (Raychem, Cabseal, 3M, Seal) | 8 | Nos |  |  |
| 22 | Supply installation testing & Commissioning of Copper wound distribution Transformer of following rating and % Impedance, 11 / 0.433KV 1600 KVA Delta-Star Connected, Vector Group Dyn 11, ONAN Cooled losses as per IS 1180 part I 2014 (Fourth Revision) Level-II, with boltless core design including standard accessories like conservator with prismatic oil level gauge , silica gel breather, Bucholz relay, pressed steel radiator fins, Radiator Valve(above 1600 Kva) Suitable size HT cable box, LT cable box with Busbar connection for outgoing cables, Off -LTC (+/- 2.5%, +/- 5% to - 7.5% ), temperature rise of 40 degree C in oil / 45 degree C in winding , drain valve, Air release device, Dial type Oil & Winding Temperature gauge with alarm & trip contacts, first filling of transformer oil as per IS :335-1953 , Epoxy primer and PU based paint as Top coat, Unidirectional rollers for rating upto 800 kva & bi- directional above 800 Kva rollers with locking arrangement etc. as required. The Transformer shall be subjected to routine factory tests (as per IS:2026 and IS:1180) including Temperature rise test in OEM’s own lab shall be witnessed by Engineer Physically. Transformer shall be tested from CTL of discom before charging of transformer & complete installaion must be certified from Electrical Inspectorate office as per Indian Electricity rule, (CTL testing charges and Electrical Inspection charges shall be reimbursed by the department to the contractor)Following tests shall be carried out on each transformer at site by OEM enginer in presence of department authorised representative:- a) Ratio test on each tapping.b) Resistance of windings at principal and all tapings.c) Insulation resistance of the winding between HV to earth / HV to LV / LV to earth.d) Vector group test.e) Magnetic Balance test. All as per pre-approved by Engineer in charge. MAKE: CROMTPON GREVES/ABB/VOLTAMP (Outdoor Type Transformer) | 1 | Nos |  |  |
| 23 | Supply and laying of 32 mm insulated rubber mat inside the HT meter cubical room. The size of rubber mat shall be 2mtrs x 1mtrs. Vendor shall share sample with Client prior placing the order. | 10 | R.Mtrs |  |  |
| 24 | Civil work for (Labour + Material) Foundation of Transformer, MS angle as per Required & AND OTHER MISCELLANEOUS CHARGES | 1 | Job |  |  |
| 25 | Approval for Electrical Inspector & JVVNL |  |  |  |  |
| a. | Electrical Inspector fee consultancy and other charges | 1 | Job |  |  |
| b. | Charges for obtaining approval/NOC from the office of Electrical Inspector, Jaipur, (other than the fee levied by the Electrical Inspector's Office) for the HT electrical installations. Fees levied by the Office of Electrical Inspector will be reimbursed by the Institute on presentation of actual receipts / paid by the institute on receiving demand notice from the office. | 1 | Job |  |  |
|  |  |  |  | Amount |  |
|  |  |  |  | GST@18% |  |
|  |  |  |  | Total |  |

GENERAL TERMS AND CONDITIONS:

- All applicable taxes such as GST must be clearly mentioned. If not specified, it shall be deemed that all such charges are included in the quoted price.

- If the supplier does not have a particular item or proposes a different make than that specified in the tender, the same must be clearly highlighted in the bid.

- Prices must be inclusive of all charges such as packing, forwarding, transit insurance, transportation, loading, unloading (up to 50 meters), installation, and any other incidental expenses.

- Bid must be submitted on an F.O.R. basis for delivery at: The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur – 302031.

- Bid shall remain valid for a minimum period of 30 days. No change in prices will be accepted during the validity period.

- The LNMIIT reserves the right to reject any quotation without assigning any reason.

- Payment terms shall be mutually decided and agreed upon between the Institute and the vendor.

- The bidder must submit a No Conflict of Interest Declaration along with the bid.

- The bid must be submitted on the company’s letterhead and in the LNMIIT-prescribed format only.

- Any item or service not being supplied by the bidder must be clearly mentioned separately in the bid.

- Vendors must provide a photocopy of their cheque/cancelled cheque along with the invoice for payment processing.

- Prices shall be quoted in Indian Rupees (INR) only.

- Total prices shall be quoted for the complete scope of work as per technical specifications, inclusive of all taxes, duties, insurance, packing, forwarding, and incidental charges.

- Agencies or individuals who are debarred or blacklisted are not permitted to participate in the tendering process. Any agency engaging a debarred person for negotiations or representation is also liable to be debarred.

- If the work is not completed within the stipulated time mentioned in the work order, the competent authority of LNMIIT reserves the right to accept partial work on suitable terms, cancel the supply/work order, withhold or stop payment, forfeit the Earnest Money Deposit, or debar the agency. The decision of the Competent Authority shall be final and binding.

- In case two or more bidders quote the same rates, the final selection shall be made through a draw of lots conducted by a committee comprising LNMIIT administrative members(PCC).

- Vendors are required to visit the site and conduct a detailed survey before submitting their bid to understand the exact requirements. No request for additional items or modifications will be entertained later.

- A pre-bid meeting and/or site visit may be arranged prior to submission of bids to clarify any doubts regarding project details, scope of work, and required documents.

Date: - 						Seal & Signature.

Name: -

Designation: -

Place: -						Mobile No.:-