Tender No:. 2026-27/Project/2B/LNM-1405
The LNM Institute of Information Technology, Jaipur

TENDER NOTICE
The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.
The institute invites proposals from competent vendors for “Temporary Hostel Mess Kitchen (Lump Sum)”. Bidders can submit their sealed offers/s at the following address by Email/Speed-Post/ Registered Post/ By-hand/courier before 05:00 PM on 12-07-2026.
Filing of Tender:
Option 1: Physical submission of offers (hard copy) in sealed envelopes.
Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the institute in person/ Speed-Post/ Registered Post/ By-hand/courier of the Institute after marking due entries in the Receipt Book available with the Security Officer at the main gate. 
The tender subject and reference number must be mentioned on the envelope. 

Director
The LNM Institute of Information Technology,
Gram – Rupa Ki Nangal, Post – Sumel,
Via – Jamdoli, Jaipur- 302031

Option 2: Password-protected online submission via Email 
Password-protected offers can be submitted by the bidders via email at the below-mentioned email IDs.

tender-document@lnmiit.ac.in (password-protected document) 
chairman.pcc-projects@lnmiit.ac.in (password only)
The tender subject and reference number must be mentioned in the subject line of the emails. 

Bid Process:
Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory, are required to be submitted in two separate envelopes/emails. 
Envelopes/Emails should be duly marked as follows: 
1. [bookmark: _Hlk219040947]Technical bid for the” Temporary Hostel Mess Kitchen” (Technical bid must be submitted without password protection)
2. [bookmark: _Hlk219038875][bookmark: _Hlk219040953]Commercial Bid for the “Temporary Hostel Mess Kitchen” (The Commercial bid must be submitted with password protection.)
3. Both Envelopes/files should be enclosed/attached in a single envelope/email bearing the heading “Bid for the “Temporary Hostel Mess Kitchen (Lump Sum)” (Tender No.: 2026-27/Project /2B/LNM-1405)”. 

Note: The bidders/vendors are requested to go through the tender document carefully and ensure compliance with all specifications/instructions in this tender
Bids are liable to be rejected: 
· If the above-mentioned bid submission procedure is not followed.
· Incomplete and non-conforming bids.
· Arbitration: All disputes and differences arising between the two parties in connection with this order shall be mutually settled as far as possible, failing which, all such disputes shall be referred to arbitration and settlement under the provision of the Arbitration and Conciliation Act, 1996 and as amended from time to time or any such law for the time being prevailing in India. The venue of such arbitration shall be Jaipur.
Technical Bid: (in a separate sealed envelope/via email)

Bid for the Temporary Hostel Mess Kitchen (Lump Sum)
(Tender No. : 2026-27/ Project /2B/LNM-1405)

Bidder is required to furnish the requisite details as per the below mentioned table format and proof of such documents to be uploaded along with the bid under respective title/ headings as mentioned at column no ‘C’ accordingly.

	S.No.
	Title/ Heading
Details sought by buyer
	Details/ Certificate No. (Attached Y/N)

	A
	B
	C

	1.
	Bidder Firm Name & Registration No,
	

	2.
	Bidder’s Company profile or brief note
	

	3.
	PAN Card No,.
	

	4.
	GST Number
	

	5.
	List of Directors/ Partners/Proprietor/ Members of the Bidder’s Firm
	

	6.
	Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members
	

	7.
	Bidder Turnover - Average annual turnover for last three years
	

	8.
	The Client List with some purchase orders and satisfactory certificate (to whom the vendor has delivered the goods/provided the services in the past (Three (03) purchase orders/work orders, at least one from each of the last three years, including the previous year.)
	

	9.
	If the bidder is authorized by the OEM/Manufacturer. Proof of the same is to be submitted with the Technical Bid
	

	10.
	An undertaking (self-certificate) that the agency has not been blacklisted by a Central/State/UT Government Institutions and there has been no litigation with any government department/institution on account of any services/supplies.
	

	11.
	Scanned copy of EMD/ Tender Fees paid through RTGS/NEFT (if required/asked in the tender)
	

	12
	Xerox copies of MoUs with previous colleges (minimum three) must be attached. (Applicable for student fest only).
	





Drawing/sample photograph (Typical)


[image: ]


Scope of work

· The scope of work will cover the supply /arrangement of given items at LNMIIT Jaipur campus.
· The Vendor is required to submit the complete documentation of the supplied item after delivery.


Signature with seal



Technical specification: 
	
	Sr. No.
	Item Name
	Qty.
	UOM

	1
	Providing and constructing a temporary all-weather Hostel Mess Kitchen Shed complete in all respects, comprising excavation and foundation work; brick masonry in superstructure & superstructure  including repair of existing brick wall wherever required; internal and external cement plaster; interior surfaces finished with approved quality enamel paint over primer and putty as required; exterior surfaces finished with approved quality weatherproof exterior acrylic paint over primer and putty as required; prefabricated steel roof framework comprising trusses, purlins, bracing, connection plates, bolts and nuts supported on the masonry structure; application of primer and synthetic enamel paint to all exposed steel members; providing and fixing 0.50 mm thick pre-coated GI roofing sheets with minimum 450 mm projection on three sides including ridge, flashing, fasteners and all necessary accessories; providing and fixing powder-coated metal false ceiling comprising aluminum/GI modular ceiling panels with suspended GI grid framework complete with hangers, perimeter trims and accessories; providing and fixing aluminum sliding windows and MS/GI access door complete with fittings and fixtures; PCC flooring base with 25 mm thick Kota stone flooring and skirting; exhaust fans and ventilation arrangements; complete internal electrification including wiring, conduits, switches, sockets, LED light fittings, exhaust fan points, distribution board, MCBs and earthing; complete plumbing and sanitary works including stainless steel sink, CP fittings, internal water supply piping, waste water piping, drainage arrangements and connection to existing water supply and drainage system up to 20 m lead; transportation, loading, unloading, erection, testing, commissioning, labour, tools and plants, scaffolding, consumables, wastage and all incidental works necessary for satisfactory completion and proper functioning of the shed, complete as per approved drawings, CPWD specifications, relevant IS codes and directions of the Engineer-in-Charge .Note: The item includes all civil, roofing, false ceiling, painting, electrical, plumbing and finishing works required for a complete and functional Hostel Mess Kitchen Shed having an approximate covered area of 33.75 Sqm (4.50 m × 7.50 m).
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Area        ( SFT)


[bookmark: _Hlk214373706]

                                                                                                     Signature with seal


Temporary hostel Mess kitchen- Tin Shed Structure Design & Specification

1. Proposed Size & Layout
Overall covered area: 4.5 m x 7.5 m
Height at eaves: 3:00 m minimum
Ridge height: 3.60 m minimum
Structure type: Temporary all- weather prefabricated hostel mess kitchen shed
Existing south side 4.5 m wall shall remain in brick masonry with two windows and exhaust arrangements.
North, east, and west side shall be brick/ block work with cement plaster including enamel paint
East and west side shall have accessible double-leaf doors/ openings.
Entire structure shall be enclosed from all sides suitable for all-weather use.
Flooring shall consist of PCC base with 25mm Kota stone finish.
Water connection shall be extended from nearby source with approximately 20 m lead.

2. Structural System
Foundation 
Brick Foundation up to 1.2-meter 1st class burnt clay conventional building bricks conforming to IS 1077-1922 having compressive strength not less than 12.5 N/mm2, 
CM 1:6 (1 Cement: 6 coarse Sand)
Should be 600 mm height from NGL level with plinth protection.
DPC as per IS code .

Steel Structure
 Truss members: ISA/ISMC sections.
Purlins; GI Z-purlin 150 mm minimum.
 spacing: Approx. 3 m c/c.
Base plate: 230x230x8 mm.
All steel members to receive one coat red oxide primer and two coats synthetic enamel paint.

Roofing & Cladding
Roof slope: Minimum 1:5.
Roofing sheet: 0.50 mm thick color-coated GI profile sheet with minimum 120 GSM zinc
coating.
Fasteners: Self-drilling screws/J-hooks with EPDM washers.
Ridge flashing, side flashing, and sealing complete.
Gl rainwater gutter with PVC down-take pipe.
Ridge ventilator arrangement with perforated GI mesh.

Weather Protection
Structure designed for all-season temporary use including rain and moderate wind condition.
All exposed steel members shall be corrosion resistant.
Necessary waterproofing and leak-proof overlapping to be ensured.

3.  Brick Masonry Wall
Existing 230 mm thick brick masonry wall on south side shall remain retained.
Wall length: 4.5 m.
Brick work in 1st class brick as pe IS code with lintel & DPC.
Necessary repair, plastering, crack filling, and finishing shall be carried out.
Internal and external plaster: 15 mm thick CM 1:4.
Existing wall to be painted with washable acrylic paint.
4. Windows, Ventilation & Exhaust
Windows
Two aluminum sliding windows shall be provided in brick wall.

Window Specification

Size: 1.20 m x 1.20 m each.
Powder-coated aluminum frame.
5 mm clear glass shutters.
Mosquito mesh and MS safety grill.
Window sill level: 900 mm.

Exhaust & Ventilation
Four heavy-duty exhaust fans of 450 mm sweep.
Two exhaust fans near cooking zone.
Two exhaust fans for cross ventilation.
Continuous ridge ventilation below roof apex with GI perforated mesh
Additional louvers above window level where required.

5. Doors & Accessibility
Main Doors
East and west sides shall be provided with accessible entry arrangements.
Proposed Arrangement
Double leaf MS framed GI sheet doors on both sides
Size
Clear opening width: 2.40 m minimum.
Height: 2.40 m minimum.
Material
18 gauge GI sheet fixed over MS frame.
Heavy-duty hinges, locking arrangement, tower bolts, handles, stoppers, and rubber buffers complete.

6. Flooring System
Ground Preparation
Surface leveling and compaction complete.
Anti-termite treatment if required.
Flooring Layers
Compacted earth filling/subgrade.
100 mm thick PCC 1:4:8.
25 mm thick Kota stone flooring.
Kota Stone Specification
Machine-cut Kota stone of minimum 25 mm thickness.
Mirror/machine polished finish.
Joint width not exceeding 3 mm.
Flooring slope: 1:100 towards drain points.
100 mm high Kota stone skirting complete.

Drainage
Floor trap and surface drain near washing area.
Proper wastewater drainage arrangement around structure.

7. Water Supply & Plumbing
Water connection from nearby existing source with approximately 20 m lead.
25 mm dia CPVC/HDPE pipe line complete.
One kitchen sink point.
One wash basin point.
One bib cock for washing/cleaning.
Isolation valve near inlet point.
Necessary clamps, excavation, cutting, restoration, and testing complete.

8. Electrical Provisions
LED batten light fittings.
Weatherproof modular switches and sockets.
Exhaust fan wiring points.
One industrial power socket for kitchen equipment.
Earthing arrangement for steel structure.
Mini distribution board with MCB complete.

9. Painting & Finishing
Steel members painted with approved synthetic enamel paint over primer.
Existing brick wall finished with acrylic washable paint.
Roof underside insulation using aluminum bubble insulation if required.
PVC rainwater pipes connected to nearest drain line.

10. Metal False Ceiling
Technical Specifications
· Tile Size: 600 × 600 mm 
· Tile Thickness: 0.5 mm minimum 
· Material: Galvanized Steel / Aluminum 
· Finish: Factory powder-coated white 
· Grid System: Exposed T-24 GI suspension grid 
· Suspension: GI hangers and rods at required spacing 
· Edge Trim: Powder-coated wall angle 
· Performance: Moisture resistant, corrosion resistant, washable, non-combustible

11. GENERAL NOTES
· The contractor shall visit the site and familiarize himself with the site conditions, existing structures, utilities, access restrictions and scope of work before quoting. 
· The quoted rate shall be inclusive of all materials, labour, machinery, tools & plants, scaffolding, transportation, loading, unloading, handling, storage, wastage, testing, commissioning and all incidental works required for complete execution of the work. 
· All materials shall be new, of approved quality and conform to the latest relevant IS Codes, CPWD Specifications and directions of the Engineer-in-Charge. 
· The work shall include excavation, foundation work, brick masonry, plastering, painting, roofing, false ceiling, flooring, electrical and plumbing works, whether specifically mentioned or otherwise required for satisfactory completion and functioning of the facility. 
· The contractor shall verify all dimensions at site before commencement of work. Any discrepancy shall be brought to the notice of the Engineer-in-Charge for clarification. 
· The prefabricated steel roof framework shall include trusses, purlins, bracing, cleats, connection plates, bolts, nuts and all accessories necessary for structural stability. 
· Roofing shall be provided using 0.50 mm thick pre-coated GI sheets including ridge pieces, flashing, fasteners, sealants and a minimum 450 mm projection on three sides complete in all respects. 
· The false ceiling shall consist of powder-coated metal ceiling tiles with complete suspension grid system, hangers, wall angles and accessories as approved by the Engineer-in-Charge. 
· Internal walls shall be finished with approved quality enamel paint over primer and putty, while external surfaces shall be finished with approved quality weatherproof exterior acrylic paint. 
· The flooring shall comprise PCC base and 25 mm thick Kota stone flooring and skirting, complete with polishing and finishing. 
· The scope includes providing and fixing aluminum sliding windows, MS/GI access door and all necessary hardware, fittings and fixtures. 
· Electrical works shall include complete internal electrification comprising conduits, wiring, switches, sockets, LED light fittings, exhaust fan points, distribution board, MCBs, earthing and all accessories required for proper functioning. 
· Plumbing and sanitary works shall include stainless steel sink, CP fittings, internal water supply piping, drainage piping and connection to existing water supply and drainage systems within a lead of 20 m. 
· Necessary openings, cut-outs, sleeves, supports and making good of finished surfaces for electrical, plumbing and other services shall be deemed included in the quoted rate. 
· The contractor shall ensure proper waterproofing, leak-proof roofing installation and weather-tight joints at all locations. 
· All exposed steel surfaces shall be cleaned, primed and painted with approved primer and synthetic enamel paint as specified. 
· The contractor shall maintain the work site in a safe and clean condition throughout the execution period and remove all debris, surplus materials and temporary structures after completion of work. 
· All safety measures, PPE, barricading, signage and statutory requirements shall be arranged by the contractor at his own cost. 
· Measurement for payment shall be on Lump Sum basis, and no extra payment shall be made for any item required for successful completion of the work but not specifically mentioned in the BOQ. 
· The work shall be completed, tested and commissioned to the satisfaction of the Engineer-in-Charge and handed over in a fully functional condition. 
· Any damage caused to existing buildings, services, roads, pavements or utilities during execution shall be repaired and restored by the contractor at no additional cost. 
· The quoted rate shall include all taxes, duties, royalties, leads, lifts and other charges applicable as per prevailing regulations, excluding GST if payable separately under the contract conditions. 
· The contractor shall submit material approvals, shop drawings (if required) and samples for approval before procurement and installation. 
· Final measurements, quality acceptance and certification shall be as per CPWD specifications and directions of the Engineer-in-Charge. 
· Approximate covered area of the shed is 33.75 Sqm (4.50 m × 7.50 m). The contractor shall execute the complete facility on a turnkey basis under the quoted Lump Sum item.

12. Suggested Approved Makes
Roofing Sheet: Tata Bluescope / JSW / Bhushan
Structural Steel: SAIL / Tata Steel
Kota Stone: Approved premium Kota stone
Aluminum Sections: Jindal or equivalent
Plumbing: Astral / Supreme / Ashirvad
Electrical: Anchor / Havells / Legrand
Metal False Ceiling : Armstrong / Hunter Douglas

13. Functional Arrangement
Cooking zone near exhaust fans.
Washing counter near water supply point.
Storage provision along existing brick wall.
Cross ventilation through ridge ventilator and exhaust fans.
Smooth circulation space for mess staff movement




Signature with seal




Annexure
To Whomsoever It May Concern
This is to confirm that we, the undersigned, intend to participate in Tender No.: 2026-27 /Project /2B/LNM-1405. for the tender/work titled: Bid for the “Temporary Hostel Mess Kitchen (Lump Sum)”
We hereby certify the following:
No Conflict of Interest:
1. We declare that we have no conflict of interest in participating in the above tender. We further confirm that we are not engaged in any activity or association that may compromise, or be perceived to compromise, our impartiality or ability to fulfil the obligations of the tender.

Undertaking on Blacklisting & Litigation (Self-Certificate):
2. We hereby undertake that:
· Our agency/firm has never been blacklisted or debarred by any Central Government, State Government, Union Territory administration, or any other Institution/Organization.
· There is no ongoing or past litigation against our agency/firm with any Central Government, State Government, Union Territory administration, or any other Institution/Organization on account of any services/supplies.
· If at any stage the above declaration is found to be false, the Institute shall have the right to take any action as deemed appropriate, including rejection of our bid.

Site Visit /Understanding:
3. We confirm that we have visited the site/clearly understood the requirements and expectations of the college authorities.

Scope of Work:
4. We have thoroughly reviewed the scope of work mentioned in the bid document. The entire inventory/requirement/work has been verified and found to be in order. We also confirm that no additional items beyond the listed inventory/requirement will be required for successful completion of the work. However, if any additional item is required during execution, the same shall be provided by us as per the requirement.


Bidder Details

Name of Bidder: ______________________________________

Address: _____________________________________________

Contact Person: _______________________________________

Mobile No.: ___________________________________________

Email ID: _____________________________________________


Authorized Signatory: __________________________________

Signature & Stamp: ____________________________________


Date: _________________
Place: ________________


Commercial Bid: (in separate sealed envelope/password protected file via email)

Bid for the Temporary Hostel Mess Kitchen (Lump Sum)
(Tender No.: 2026-27/ Project /2B/LNM-1405)


	S.No.
	Item Name/ Description
	Qty.
	UOM
	Rate
	Amount

	1.
	Providing and constructing a temporary all-weather Hostel Mess Kitchen Shed complete in all respects, comprising excavation and foundation work; brick masonry in superstructure & superstructure  including repair of existing brick wall wherever required; internal and external cement plaster; interior surfaces finished with approved quality enamel paint over primer and putty as required; exterior surfaces finished with approved quality weatherproof exterior acrylic paint over primer and putty as required; prefabricated steel roof framework comprising trusses, purlins, bracing, connection plates, bolts and nuts supported on the masonry structure; application of primer and synthetic enamel paint to all exposed steel members; providing and fixing 0.50 mm thick pre-coated GI roofing sheets with minimum 450 mm projection on three sides including ridge, flashing, fasteners and all necessary accessories; providing and fixing powder-coated metal false ceiling comprising aluminum/GI modular ceiling panels with suspended GI grid framework complete with hangers, perimeter trims and accessories; providing and fixing aluminum sliding windows and MS/GI access door complete with fittings and fixtures; PCC flooring base with 25 mm thick Kota stone flooring and skirting; exhaust fans and ventilation arrangements; complete internal electrification including wiring, conduits, switches, sockets, LED light fittings, exhaust fan points, distribution board, MCBs and earthing; complete plumbing and sanitary works including stainless steel sink, CP fittings, internal water supply piping, waste water piping, drainage arrangements and connection to existing water supply and drainage system up to 20 m lead; transportation, loading, unloading, erection, testing, commissioning, labour, tools and plants, scaffolding, consumables, wastage and all incidental works necessary for satisfactory completion and proper functioning of the shed, complete as per approved drawings, CPWD specifications, relevant IS codes and directions of the Engineer-in-Charge .Note: The item includes all civil, roofing, false ceiling, painting, electrical, plumbing and finishing works required for a complete and functional Hostel Mess Kitchen Shed having an approximate covered area of 33.75 Sqm (4.50 m × 7.50 m).
	

























364
	


























  Area
   (SFT)
	
	

	Total
	

	GST
	

	Total including GST
	






GENERAL TERMS AND CONDITIONS:
1. All applicable taxes such as GST must be clearly mentioned. If not specified, it shall be deemed that all such charges are included in the quoted price.
2. If the supplier does not have a particular item or proposes a different make than that specified in the tender, the same must be clearly highlighted in the bid.
3. Prices must be inclusive of all charges such as packing, forwarding, transit insurance, transportation, loading, unloading (up to 50 meters), installation, and any other incidental expenses.
4. Bid must be submitted on an F.O.R. basis for delivery at: The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur – 302031.
5. Bid shall remain valid for a minimum period of 60 days. No change in prices will be accepted during the validity period.
6. The LNMIIT reserves the right to reject any quotation without assigning any reason.
7. Payment terms shall be mutually decided and agreed upon between the Institute and the vendor.
8. The bidder must submit a No Conflict-of-Interest Declaration along with the bid.
9. The bid must be submitted on the company’s letterhead and in the LNMIIT-prescribed format only.
10. Any item or service not being supplied by the bidder must be clearly mentioned separately in the bid.
11. Vendors must provide a photocopy of their cheque/cancelled cheque along with the invoice for payment processing.
12. Prices shall be quoted in Indian Rupees (INR) only.
13. Total prices shall be quoted for the complete scope of work as per technical specifications, inclusive of all taxes, duties, insurance, packing, forwarding, and incidental charges.
14. Agencies or individuals who are debarred or blacklisted are not permitted to participate in the tendering process. Any agency engaging a debarred person for negotiations or representation is also liable to be debarred.
15. If the work is not completed within the stipulated time mentioned in the work order, the competent authority of LNMIIT reserves the right to accept partial work on suitable terms, cancel the supply/work order, withhold or stop payment, forfeit the Earnest Money Deposit, or debar the agency. The decision of the Competent Authority shall be final and binding.
16. In case two or more bidders quote the same rates, the final selection shall be made through a draw of lots conducted by a committee comprising LNMIIT administrative members (PCC).
17. Vendors are required to visit the site and conduct a detailed survey before submitting their bid to understand the exact requirements. No request for additional items or modifications will be entertained later.
18. A pre-bid meeting and/or site visit may be arranged prior to submission of bids to clarify any doubts regarding project details, scope of work, and required documents.




Signature with seal
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