Tender No:. 2026-27/Sports/2B/LNM-1486
The LNM Institute of Information Technology, Jaipur

TENDER NOTICE
The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.
The institute invites proposals from competent vendors for Supply, Installation, Testing & Commissioning (SITC) of Class-III LED Sports Flood Lighting System for Football Ground at LNMIIT. Bidders can submit their sealed offers/s at the following address by Email/Speed-Post/ Registered Post/ By-hand/courier before 05:00 PM on 31st July 2026.
Filing of Tender:
Option 1: Physical submission of offers (hard copy) in sealed envelopes.
Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the institute in person/ Speed-Post/ Registered Post/ By-hand/courier of the Institute after marking due entries in the Receipt Book available with the Security Officer at the main gate. 
The tender subject and reference number must be mentioned on the envelope. 

Director
The LNM Institute of Information Technology,
Gram – Rupa Ki Nangal, Post – Sumel,
Via – Jamdoli, Jaipur- 302031

Option 2: Password-protected online submission via Email 
Password-protected offers can be submitted by the bidders via email at the below-mentioned email IDs.

tender-document@lnmiit.ac.in (password-protected document)
tender-password@lnmiit.ac.in (password only)
The tender subject and reference number must be mentioned in the subject line of the emails. 

Bid Process:
Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory, are required to be submitted in two separate envelopes/emails. 
Envelopes/Emails should be duly marked as follows: 
1. [bookmark: _Hlk219040947]Technical bid for the “Supply, Installation, Testing & Commissioning (SITC) of Class-III LED Sports Flood Lighting System for Football Ground at LNMIIT”. (Technical bid must be submitted without password protection)
2. [bookmark: _Hlk219038875][bookmark: _Hlk219040953]Commercial Bid for the “Supply, Installation, Testing & Commissioning (SITC) of Class-III LED Sports Flood Lighting System for Football Ground at LNMIIT” (The Commercial bid must be submitted with password protection.)
Both Envelopes/files should be enclosed/attached in a single envelope/email bearing the heading “Bid for the “Supply, Installation, Testing & Commissioning (SITC) of Class-III LED Sports Flood Lighting System for Football Ground at LNMIIT”) (Tender No. : 2026-27/Sports/2B/LNM1486)”. 
Note: The bidders/vendors are requested to go through the tender document carefully and ensure compliance with all specifications/instructions in this tender
Bids are liable to be rejected: 
· If the above-mentioned bid submission procedure is not followed.
· Incomplete and non-conforming bids.
· Arbitration: All disputes and differences arising between the two parties in connection with this order shall be mutually settled as far as possible, failing which, all such disputes shall be referred to arbitration and settlement under the provision of the Arbitration and Conciliation Act, 1996 and as amended from time to time or any such law for the time being prevailing in India. The venue of such arbitration shall be Jaipur.
Technical Bid: (in a separate sealed envelope/via email) 
Bid for the Supply, Installation, Testing & Commissioning (SITC) of Class-III LED Sports Flood Lighting System for Football Ground at LNMIIT
(Tender No. : 2026-27/Sports/2B/LNM-1486)

Bidder is required to furnish the requisite details as per the below mentioned table format and proof of such documents to be uploaded along with the bid under respective title/ headings as mentioned at column no ‘C’ accordingly.

	S.No.
	Title/ Heading
Details sought by buyer
	Details/ Certificate No. (Attached Y/N)

	A
	B
	C

	1.
	Bidder Firm Name & Registration No,
	

	2.
	Bidder’s Company profile or brief note
	

	3.
	PAN Card No,.
	

	4.
	GST Number
	

	5.
	List of Directors/ Partners/Proprietor/ Members of the Bidder’s Firm
	

	6.
	Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members
	

	7.
	Bidder Turnover - Average annual turnover for last three years
	

	8.
	The Client List with some purchase orders and satisfactory certificate (to whom the vendor has delivered the goods/provided the services in the past (Three (03) purchase orders/work orders, at least one from each of the last three years, including the previous year.)
	

	9.
	If the bidder is authorized by the OEM/Manufacturer. Proof of the same is to be submitted with the Technical Bid
	

	10.
	An undertaking (self-certificate) that the agency has not been blacklisted by a Central/State/UT Government Institutions and there has been no litigation with any government department/institution on account of any services/supplies.
	

	11.
	Scanned copy of EMD/ Tender Fees paid through RTGS/NEFT (if required/asked in the tender)
	

	12
	Xerox copies of MoUs with previous colleges (minimum three) must be attached. (Applicable for student fest only).
	







1. Scope of Work
The scope of work shall include, but shall not be limited to:
· Design verification and preparation of lighting layout using software. 
· Preparation of shop drawings, cable layout, foundation details and Single Line Diagram (SLD). 
· Supply of all LED flood lights, poles, cross arms, distribution panel, cables, earthing materials, junction boxes and all associated accessories. 
· Excavation, RCC foundations, reinforcement, anchor bolt fixing, pole erection and restoration of site. 
· Supply and laying of LT armoured cables including trenching, sand cushioning, brick protection, warning tape and backfilling. 
· Installation of LED flood lights, distribution panel, protection devices, earthing system and all electrical accessories. 
· Testing, commissioning, lux measurement, aiming of fixtures and performance verification. 
· Submission of as-built drawings, warranty certificates, test reports, operation & maintenance manuals and other completion documents. 
The work shall include all labour, transportation, tools, tackles, consumables and accessories required for complete installation, whether specifically mentioned or otherwise required for proper functioning of the system.

2. Bill of Quantities (BOQ)
	Sr. No.
	Description
	Qty
	Unit

	1
	200W Sports LED Flood Light Fixture, minimum 130 lm/W, IP66, IK08, 6500K, surge protection ≥10kV, 24 Narrow Beam (~30°) & 24 Wide Beam (~60°–90°)
	48
	Nos

	2
	10 m Hot Dip Galvanized Octagonal Steel Pole complete with cross arm, terminal box, RCC foundation, anchor bolts and all accessories
	6
	Nos

	3
	Outdoor Weatherproof Main Distribution Board (IP65) complete with 63A TPN MCB, RCCB/ELCB, SPD, digital meters and astronomical timer
	1
	No

	4
	20A DP 10kA MCB inside pole terminal box
	6
	Nos

	5
	4 Core × 25 sq.mm Aluminium XLPE Armoured Cable
	500
	Mtr

	6
	4 Core × 4 sq.mm Copper XLPE Armoured Cable
	90
	Mtr

	7
	3 Core × 2.5 sq.mm Copper Flexible Cable
	100
	Mtr

	8
	Maintenance Free Chemical Earthing Set complete with chamber and accessories
	8
	Sets

	9
	Cable trenching, sand cushioning, protective brick covering and backfilling
	500
	Mtr

	10
	15 Meter Hot Dip Galvanized Octagonal Steel Pole complete with cross arm, terminal box, RCC foundation, anchor bolts and all accessories
	Rate Only
	



The quoted rates shall include all transportation, loading, unloading, installation, testing, commissioning and all incidental items required for completion of the work.
3. Technical Specifications
LED Flood Lights
· Power: 200 W 
· Minimum efficacy: 130 lm/W 
· Input Voltage: 140–270 V AC 
· Power Factor: ≥0.95 
· THD: ≤10% 
· CRI: ≥70 
· Colour Temperature: 6500 K 
· Protection: IP66, IK08 
· Integrated Surge Protection: Minimum 10 kV 
· Die-cast aluminium housing with toughened glass 
· LM-79 & LM-80 tested LEDs 
· BIS approved product 
· High efficiency driver with short circuit, overload and thermal protection 

Lighting Arrangement
· Total Fixtures: 48 Nos 
· 24 Nos Narrow Beam (≈30°) 
· 24 Nos Wide Beam (≈60°–90°) 
· Mounted on 6 poles, 8 fixtures per pole. 
Steel Poles
· Height: 10 meters 
· Octagonal steel construction 
· Hot dip galvanized (minimum 86 micron coating) 
· Designed for minimum 180 km/hr wind speed 
· Complete with mounting brackets, terminal box, cable entry and foundation hardware. 
Main Distribution Board
Outdoor IP65 enclosure complete with:
· 63A TPN Incomer MCB 
· RCCB/ELCB (300 mA) 
· Two 32A TPN outgoing feeders 
· Digital voltmeter & ammeter 
· Phase indication lamps 
· Astronomical timer 
· Surge Protection Device (SPD) 
Earthing
Maintenance-free chemical earthing comprising copper bonded electrode, earth enhancement compound, inspection chamber and earth strip/wire. Maximum earth resistance shall not exceed 1 Ohm.

4. Performance Requirements
The completed system shall comply with Class-III Football Lighting Standards and shall provide uniform illumination suitable for training and local competitive matches.
The bidder shall submit:
· Dialux/Relux simulation 
· Lux calculation report 
· Fixture aiming details 
· Lighting layout 

Final payment shall be made only after satisfactory lux measurement and successful commissioning.

5. Eligibility Criteria
The bidder shall possess:
· Minimum 5 years' experience in Sports Flood Lighting works. 
· Successfully completed similar works during the last five years: 
· Three works costing at least 40% of the estimated value, or 
· Two works costing at least 60%, or 
· One work costing at least 80%. 
· Valid GST Registration. 
· PAN. 
· Electrical Contractor Licence. 
· OEM Authorization for LED fixtures. 
· Average annual turnover of ₹50 Lakhs or above during the last three financial years. 

6. Completion Period
The entire work shall be completed within 30 days from the date of issue of the Work Order.

7. Testing & Commissioning
The contractor shall conduct:
· Insulation Resistance Test 
· Earth Resistance Test 
· Functional Testing 
· Load Testing 
· Lux Measurement 
· Trial Run 
All test reports shall be submitted before final acceptance.
8. Warranty
The complete lighting system shall carry a minimum comprehensive warranty of five (5) years from the date of successful commissioning.
The warranty shall cover LED luminaires, drivers, surge protection devices, poles, distribution panel, cables, earthing system and all supplied accessories. Any defect arising during the warranty period shall be rectified or the defective component replaced within seven (7) days, without any additional cost to the Institute.

9. Liquidated Damages
Delay in completion shall attract Liquidated Damages @ 0.5% of the contract value per week, subject to a maximum of 10% of the total contract value.

10. General Terms & Conditions
· The work shall be executed on a complete turnkey basis. 
· All materials shall be new, genuine and sourced from reputed manufacturers. 
· The contractor shall ensure compliance with the latest IS, IEC, CEA, CPWD and NBC standards. 
· The Institute reserves the right to inspect materials at any stage and reject any item not conforming to the specifications. 
· All tools, tackles, lifting equipment, scaffolding, consumables and safety equipment shall be arranged by the contractor. 
· Any damage caused to existing structures, services or utilities during execution shall be repaired by the contractor at no extra cost. 
· The contractor shall maintain proper housekeeping and adhere to all applicable safety regulations throughout the execution of the work. 
· The contractor shall submit all as-built drawings, manufacturer warranties, test certificates, operation & maintenance manuals and completion reports before final handover. 
· The Institute reserves the right to increase or decrease the quantities, accept or reject any or all bids without assigning any reason, and to cancel the tender wholly or partly without incurring any liability.

Technical specification: 
	
	Sr. No.
	Item Name
	Qty.
	UOM

	1
	200W Sports LED Flood Light Fixture, minimum 130 lm/W, IP66, IK08, 6500K, surge protection ≥10kV, 24 Narrow Beam (~30°) & 24 Wide Beam (~60°–90°)
	48
	Nos

	2
	10 m Hot Dip Galvanized Octagonal Steel Pole complete with cross arm, terminal box, RCC foundation, anchor bolts and all accessories
	6
	Nos

	3
	Outdoor Weatherproof Main Distribution Board (IP65) complete with 63A TPN MCB, RCCB/ELCB, SPD, digital meters and astronomical timer
	1
	No

	4
	20A DP 10kA MCB inside pole terminal box
	6
	Nos

	5
	4 Core × 25 sq.mm Aluminium XLPE Armoured Cable
	500
	Mtr

	6
	4 Core × 4 sq.mm Copper XLPE Armoured Cable
	90
	Mtr

	7
	3 Core × 2.5 sq.mm Copper Flexible Cable
	100
	Mtr

	8
	Maintenance Free Chemical Earthing Set complete with chamber and accessories
	8
	Sets

	9
	Cable trenching, sand cushioning, protective brick covering and backfilling
	500
	Mtr

	10
	15 Meter Hot Dip Galvanized Octagonal Steel Pole complete with cross arm, terminal box, RCC foundation, anchor bolts and all accessories
	Rate Only
	


[bookmark: _Hlk214373706]

                                                                                                     Signature with seal


Annexure
To Whomsoever It May Concern
This is to confirm that we, the undersigned, intend to participate in Tender No. : 2026-27/Sports/2B/LNM-1486 for the tender/work titled: “Supply, Installation, Testing & Commissioning (SITC) of Class-III LED Sports Flood Lighting System for Football Ground at LNMIIT”

We hereby certify the following:
No Conflict of Interest:
1. We declare that we have no conflict of interest in participating in the above tender. We further confirm that we are not engaged in any activity or association that may compromise, or be perceived to compromise, our impartiality or ability to fulfil the obligations of the tender.

Undertaking on Blacklisting & Litigation (Self-Certificate):
2. We hereby undertake that:
· Our agency/firm has never been blacklisted or debarred by any Central Government, State Government, Union Territory administration, or any other Institution/Organization.
· There is no ongoing or past litigation against our agency/firm with any Central Government, State Government, Union Territory administration, or any other Institution/Organization on account of any services/supplies.
· If at any stage the above declaration is found to be false, the Institute shall have the right to take any action as deemed appropriate, including rejection of our bid.

Site Visit /Understanding:
3. We confirm that we have visited the site/clearly understood the requirements and expectations of the college authorities.
Scope of Work:
4. We have thoroughly reviewed the scope of work mentioned in the bid document. The entire inventory/requirement/work has been verified and found to be in order. We also confirm that no additional items beyond the listed inventory/requirement will be required for successful completion of the work. However, if any additional item is required during execution, the same shall be provided by us as per the requirement.

Bidder Details

Name of Bidder: ______________________________________

Address: _____________________________________________

Contact Person: _______________________________________

Mobile No.: ___________________________________________

Email ID: _____________________________________________

Authorized Signatory: __________________________________

Signature & Stamp: ____________________________________


Date: _________________
Place: ________________
Commercial Bid: (in separate sealed envelope/password protected file via email)

Bid for Supply, Installation, Testing & Commissioning (SITC) of Class-III LED Sports Flood Lighting System for Football Ground at LNMIIT
(Tender No. : 2026-27/Sports/2B/LNM-1486)

	S.No.
	Item Name/ Description
	Qty.
	UOM
	Rate
	Amount

	1
	200W Sports LED Flood Light Fixture, minimum 130 lm/W, IP66, IK08, 6500K, surge protection ≥10kV, 24 Narrow Beam (~30°) & 24 Wide Beam (~60°–90°)
	48
	Nos
	
	

	2
	10 m Hot Dip Galvanized Octagonal Steel Pole complete with cross arm, terminal box, RCC foundation, anchor bolts and all accessories
	6
	Nos
	
	

	3
	Outdoor Weatherproof Main Distribution Board (IP65) complete with 63A TPN MCB, RCCB/ELCB, SPD, digital meters and astronomical timer
	1
	No
	
	

	4
	20A DP 10kA MCB inside pole terminal box
	6
	Nos
	
	

	5
	4 Core × 25 sq.mm Aluminium XLPE Armoured Cable
	500
	Mtr
	
	

	6
	4 Core × 4 sq.mm Copper XLPE Armoured Cable
	90
	Mtr
	
	

	7
	3 Core × 2.5 sq.mm Copper Flexible Cable
	100
	Mtr
	
	

	8
	Maintenance Free Chemical Earthing Set complete with chamber and accessories
	8
	Sets
	
	

	9
	Cable trenching, sand cushioning, protective brick covering and backfilling
	500
	Mtr
	
	

	10
	15 Meter Hot Dip Galvanized Octagonal Steel Pole complete with cross arm, terminal box, RCC foundation, anchor bolts and all accessories
	Rate Only
	
	
	

	Total
	

	GST
	

	Total including GST
	


GENERAL TERMS AND CONDITIONS:
1. All applicable taxes such as GST must be clearly mentioned. If not specified, it shall be deemed that all such charges are included in the quoted price.
2. If the supplier does not have a particular item or proposes a different make than that specified in the tender, the same must be clearly highlighted in the bid.
3. Prices must be inclusive of all charges such as packing, forwarding, transit insurance, transportation, loading, unloading (up to 50 meters), installation, and any other incidental expenses.
4. Bid must be submitted on an F.O.R. basis for delivery at: The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur – 302031.
5. Bid shall remain valid for a minimum period of 30 days. No change in prices will be accepted during the validity period.
6. The LNMIIT reserves the right to reject any quotation without assigning any reason.
7. Payment terms shall be mutually decided and agreed upon between the Institute and the vendor.
8. The bidder must submit a No Conflict of Interest Declaration along with the bid.
9. The bid must be submitted on the company’s letterhead and in the LNMIIT-prescribed format only.
10. Any item or service not being supplied by the bidder must be clearly mentioned separately in the bid.
11. Vendors must provide a photocopy of their cheque/cancelled cheque along with the invoice for payment processing.
12. Prices shall be quoted in Indian Rupees (INR) only.
13. Total prices shall be quoted for the complete scope of work as per technical specifications, inclusive of all taxes, duties, insurance, packing, forwarding, and incidental charges.
14. Agencies or individuals who are debarred or blacklisted are not permitted to participate in the tendering process. Any agency engaging a debarred person for negotiations or representation is also liable to be debarred.
15. If the work is not completed within the stipulated time mentioned in the work order, the competent authority of LNMIIT reserves the right to accept partial work on suitable terms, cancel the supply/work order, withhold or stop payment, forfeit the Earnest Money Deposit, or debar the agency. The decision of the Competent Authority shall be final and binding.
16. In case two or more bidders quote the same rates, the final selection shall be made through a draw of lots conducted by a committee comprising LNMIIT administrative members(PCC).
17. Vendors are required to visit the site and conduct a detailed survey before submitting their bid to understand the exact requirements. No request for additional items or modifications will be entertained later.
18. A pre-bid meeting and/or site visit may be arranged prior to submission of bids to clarify any doubts regarding project details, scope of work, and required documents.



Signature with seal

