The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

“The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, setup as a Non Profit Making institute located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposal from competent vendors for “Supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricated Stand”. Bidders can submit their sealed offer/s at the following address by Speed-Post/ Registered Post/ By-hand (but not by Courier) before 05:00 PM on 31.08.2022.

Bids shall be addressed to the undersigned and deposited in the tender box available at main gate of Institute after marking due entries.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Email: directoroffice@lnmiit.ac.in

Bidders can also submit their offer/s via Email with password protected document/file at the below mentioned email IDs (E-mail must sent on both mail ID) before 05:00 PM on 31.08.2022.

The Password protected document/file to be sent to purchase officer at the email id: purchase.officer@lnmiit.ac.in and password should be sent to Chairman-PCC at the email id: chairman.pcc@lnmiit.ac.in .

purchase.officer@lnmiit.ac.in

chairman.pcc@lnmiit.ac.in

Bid Process:

Techno-commercial offer shall be enclosed in envelopes/ files, duly marked as “Techno-commercial Bid for supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricated Stand” Bids are liable to be rejected if required information is not found with the offer.

Bid for Supply, Installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricate Stand

| S. No. | Particulars | Make | Qty. | UOM | Rate | Amount |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Supply, Instruction, testing and commissioning of 10 KVA Single Phase online UPS System with two year warranty | Numeric Onfinito | 2 | Nos. |  |  |
| 1 | SMF UPS Battery 26 ah/12V with MS Fabricate Stand | Exide/ Amaron | 32 | Nos. |  |  |
|  | Total |  |  |  |  |  |
|  | GST_______ |  |  |  |  |  |
| TOTAL (including taxes) |  |  |  |  |  |  |

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- The prices should be including all (Packing, forwarding, Transit Insurance, Transportation Loading/unloading and Installation etc.)

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- Bid should be valid for a minimum period of 30 days.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on company’s letterhead.

- Vendor should provide photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT

- Copy of authorization/certificate from the OEM in case supplied by a vendor who is not a manufacturer of the product (battery & UPS).

All charges applicable shall be clearly mentioned with the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final and nothing extra shall be paid extra.

Signature with seal

| Technical Specifications of UPS System |  |  |
| --- | --- | --- |
| S/No | Specification | Parameter requirements |
|  | Make | Numeric |
|  | Model | Numeric Onfiniti |
| 1. | UPS Capacity | 10 kVA |
| 2. | Technology | a. True online double conversion b. IGBT based rectifier & inverter c. Inbuilt PRS kit for Parallel Option in future |
| 3. | Input Parameters: |  |
| a. | Voltage | 230 VAC, 1 Phase |
| b. | Voltage Range | 110V to 300 VAC based on load level |
| c. | Frequency | 50 Hz |
| d. | Power Factor at rated load | Unity at full load |
| e. | Current Harmonic Distortion | Less than 10% |
| 4. | Output Parameters: |  |
| a. | Voltage | 220/230/240 VAC +/ - 1%, 1 Phase |
| b. | Frequency | 50 Hz +/- 0.25 Hz (in Battery Mode) +/- 6% (in Sync) |
| c. | THD v | < 2 % for Linear Load ; < 5 % for Non Linear Load |
| d. | Overload rating | 105 to 109 % - 10 min ; 110 to 129 % - 60 sec ; 150 % - 10 seconds |
| e. | Output waveform | Pure sinewave |
| f. | Crest Factor | 3 : 1 |
| g. | Output Power Factor | 0.9 |
| h. | Over all Efficiency | >93% without Transformer |
| 5. | Battery Parameters: |  |
| a. | Batteries Type ( 12V VRLA) | Sealed Maintenance Free Batteries ( Exide ) |
| e. | Backup Time | 30 Mins. |
| f. | DC Voltage | 192 VDC |
| h. | Battery Rack | Battery Rack / Stand |
| i. | Transfer time | UPS to Battery Mode : 0 ms |
| j | Three Stage Charger | Constant Voltage / Constant Current / Float Charging with Temperature Compensated Charger |
| k | Charging Capacity | 10 % of the Battery AH Capacity |
| 6. | Bypass: |  |
|  | Static Bypass | Required (Inbuilt) |
|  | Transfer time | < 4 ms in Sync Mode |
|  | Bypass parameter configurable via front panel | Required |
|  | Manual Bypass | Required (Inbuilt) |
| 7. | LCD Display / Alarm / Protection |  |
| a. | Metering Data |  |
|  |  | Input Voltage |
|  |  | Input Frequency |
|  |  | Output Voltage |
|  |  | Output Frequency |
|  |  | Output Power in Watts |
|  |  | Output Current |
|  |  | Load Level in % |
|  |  | Battery Voltage |
|  |  | Battery Level |
|  |  | Temperature |
|  |  | Event Log |
|  |  | Battery Test |
| b. | Status Information Data |  |
|  |  | Normal |
|  |  | Bypass |
|  |  | Battery |
|  |  | Fault |
|  |  | Converter Mode |
|  |  | Eco Mode |
|  |  | Bypass Mode |
|  |  | Battery Mode |
| c. | Fault / Waring Indication |  |
|  |  | Over Load |
|  |  | Charger Fail |
|  |  | Inverter Fault |
|  |  | Over Temperature |
|  |  | Short Circuit |
|  |  | DC low / High |
|  |  | Output Low / High |
|  |  | Fan Fail |
|  |  | Battery Disconnected |
| d. | Protection Required | Input High / Low |
|  |  | Over Load |
|  |  | Short Circuit |
|  |  | Over Temperature |
|  |  | Battery Over Charge |
|  |  | Battery Deep Discharge |
| e. | Audible Alarm | Battery Mode |
|  |  | Low Battery |
|  |  | Fault |
|  |  | Over Load |
|  |  | Bypass Mode |
| 8. | Other Features: |  |
| a. | Communication Port | RS 232 & USB |
| b. | Cold Start | Required |
| c. | Auto Restart | Required |
| d. | EPO | Required |
| e. | Generator Compatibility | Required |
| f. | SNMP Card | Optional |
| g. | Operating Temperature | 0 to 45 Deg C without derating |
| h. | Storage Temperature | 0 to 60 Deg C |
| i. | Humidity | upto 95 % |
| j. | Altitude | < 1000 meters |
| 9. | Connection |  |
|  | Input | Terminal Block |
|  | Output | Terminal Block |
|  | Battery | Terminal Block |
| 10. | Credential / Reports |  |
|  | ISO 9001 2015 | Copies Required |
|  | ISO 14001 2004 | Copies Required |
|  | ISO 45001: 2018 | Copies Required |
|  | BIS Certificate | Copies Required |
|  | JIS 8702C for battery | Copies Required |
|  | Manufacturing facility | a. Make in India. b. OEM Minimum 10 Years presence in India. |
|  | Service facility | UPS manufactures should have not less than 200 service centers accross India. |
|  | Turn Over | Vendor should have turn over more than 300 crores |
| 11. | Warranty /After Sales Support |  |
|  | Service Support | Directly from OEM for UPS & Batteries Both |
|  | Warranty | Onsite 24 Months on UPS & Batteries |
|  | Numeric Authorized service center | Local Authorized service center in Jaipur |
|  | Authorized Supplier Certificate | Numeric |