The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “Servicing of DG Sets (125 KVA/380 KVA/ 625 KVA) ”.  Bidders can submit their sealed offer/s at the following address by Speed-Post/ Registered Post/ By-hand (but not by Courier)/ before 05:00 PM on 05.03.2023.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the Institute after marking due entries.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Email: directoroffice@lnmiit.ac.in

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory are required to be submitted in two separate envelopes/files. Both envelopes/files should be duly marked as “Technical bid Servicing of DG Sets (125 KVA/380 KVA/ 625 KVA)” and “Commercial Bid for Servicing of DG Sets (125 KVA/380 KVA/ 625 KVA)” respectively. Both Envelopes shall be enclosed in a single envelope bearing the heading “Bid for Servicing of DG Sets (125 KVA/380 KVA/ 625 KVA)”. Bids are liable to be rejected if any or both of the technical or commercial offers are found in open condition or required information is not found with the offer.

Technical Bid: (in a separate sealed envelope)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turn over for the last three years to be mentioned. (Copy to be enclosed)

- List of the client to whom the vendor has delivered the goods or provided the services in past.

- Specification as mentioned below, shall be provided as per the details given below:

Scope of work, Technical data sheet and Specification of the item/s

Servicing of DG sets at LNMIIT, JAIPUR.

Servicing of DG Sets including supply of material”, for 125 KVA, 380 KVA and 625 KVA Sudhir Make DG Sets.

Tenderer should undertake below mentioned work while carrying out B-Check & servicing of the DG Sets:

- Scope of Work:

- Drain lubrication oil and replenish with the correct grade of oil.

- Change lubricating oil filter elements and fuel filter elements.

- Clean out air filter element or replace.

- Check valve clearance and adjust.

- Grease all points as required.

- Drain and flush cooling system, refill with clean water/coolant and add cooling system conditioner.

- Check water jacket heater operation.

- Check condition of fuel pipes and water hoses.

- Check for water build up in the fuel filter water trap.

- Check and adjust to specification battery voltage, charge rate and perform voltage drop test to determine condition of batteries.

- Grease fan drive and alternator bearing.

- Check functioning of changing alternator.

- Engine safety viz., high water temperature gauge, oil pressure gauge, oil temperature gauge and high speed gauge shall be checked for their functions.

- Coolant level and conditioning of coolant shall be checked and refilled.

- Check fan and alternator drive belts and tightened.

- The governor shall be checked and tuned for proper functioning.

- Check for leaks if any and shall be rectified.

- The engine shall be run on no load or at available load, check any leakage and abnormal noise.

- Check reports shall be submitted.

- Servicing of Alternator.

- Material to be used:

| S No. | Material Name | UOM | Qty. |
| --- | --- | --- | --- |
| A | 125 KVA Generator Service Work |  |  |
| 1 | B Check Kit, 6BTA ( Diesel & Oil Filter ) | Each | 1 |
| 2 | Lube oil VALVOLINE PREMIUM BLUE _20 Ltr | Each | 20 |
| 3 | KIT AIR FILTER ELEMENT | Each | 1 |
| 4 | BATTERY 12V65 AH, CUMMINS | Nos. | 1 |
| 5 | BATTERY CHARGER 12V,10AMP | Nos. | 1 |
| 6 | Inhibitor, Corrosion _ 5 ltr | Each | 1 |
| 7 | Service Charges | Each | 1 |
| B | 380 KVA Generator Service Work |  |  |
| 1 | B Check Kit, KTA-1150 ( Diesel & Oil Filter ) | Each | 1 |
| 2 | ENGINE OIL 15W40 - 55 LTR | Each | 1 |
| 3 | KIT AIR FILTER ELEMENT | Each | 1 |
| 4 | Lube Oil Fill Cover Gasket | Each | 1 |
| 5 | Cam Flo Housing Gaskit | Each | 1 |
| 6 | Corrosion Inhibitor _ 15 ltr | Each | 1 |
| 7 | Battery 12V , 80 AH Cummins/Exide _ 2 Nos. | Each | 1 |
| 8 | Battery Charger 24V, 10Amper | Each | 1 |
| 9 | Service Charges | Each | 1 |
| C | 625 KVA Generator Service Work |  |  |
| 1 | B Check Kit, V/VT/VTA_28 ( Diesel & Oil Filter ) | Each | 1 |
| 2 | ENGINE OIL 15W40 – 110 LTR | Each | 1 |
| 3 | KIT AIR Cleaner Element | Each | 1 |
| 4 | Inhibitor Corrosion 205 Liters | Each | 1 |
| 5 | Battery 12V , 80 AH Cummins/Exide_ 2 Nos. | Each | 1 |
| 6 | Battery Charger 24V, 10Amper | Each | 1 |
| 7 | Service Charges | Each | 1 |
| 8 | VAN Service Charges | Each | 1 |

Commercial Bid: (in separate sealed envelope)

Servicing of DG Sets (125 KVA/380 KVA/ 625 KVA)

| S.No. | Item Name/ Description | Make /Specification | Qty. | UOM | Rate | Amount |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 125 KVA Generator Service Work | As per technical bid | 1 | Nos. |  |  |
| 2. | 380 KVA Generator Service Work | As per technical bid |  |  |  |  |
| 3 | 625 KVA Generator Service Work | As per technical bid |  |  |  |  |
| Total |  |  |  |  |  |  |
| GST |  |  |  |  |  |  |
| Total including GST |  |  |  |  |  |  |

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should be including all (Packing, forwarding, Transit Insurance, Transportation Loading/unloading, Installation etc.). Loading/unloading up to 50 Mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- Bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

All charges applicable shall be clearly mentioned with the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

Signature with seal