The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “Servicing of LT & HT Panel, VCB, ACB , Capacitor Bank, DG Set Alternator Earthing Testing and Transformers”.  Bidders can submit their sealed offer/s at the following address by Speed-Post/ Registered Post/ By-hand (but not by Courier)/ before 05:00 PM on 16.04.2023.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the Institute after marking due entries.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Email: directoroffice@lnmiit.ac.in

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory are required to be submitted in two separate envelopes/files. Both envelopes/files should be duly marked as “Technical bid Servicing of LT & HT Panel, VCB, ACB , Capacitor Bank, DG Set Alternator Earthing Testing and Transformers” and “Commercial Bid for Servicing of LT & HT Panel, VCB, ACB , Capacitor Bank, DG Set Alternator Earthing Testing and Transformers” respectively. Both Envelopes shall be enclosed in a single envelope bearing the heading “Bid for Servicing of LT & HT Panel, VCB, ACB , Capacitor Bank, DG Set Alternator Earthing Testing and Transformers”. Bids are liable to be rejected if any or both of the technical or commercial offers are found in open condition or required information is not found with the offer.

Technical Bid: (in a separate sealed envelope)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turn over for the last three years to be mentioned. (Copy to be enclosed)

- List of the client to whom the vendor has delivered the goods or provided the services in past.

- Specification as mentioned below, shall be provided as per the details given below:

Scope of work, Technical data sheet and Specification of the item/s

Terms and conditions

- Warranty should be as per mentioned in the Technical specification.

- The Bidder should have a Branch office in Jaipur, Rajasthan.

- List of Projects of similar nature with Copies of the work orders and completion certificates successfully executed for similar work during the last 3 years.

- Guarantee - The successful bidder shall guarantee all equipment parts, materials and workmanship furnished for the installation for a period of one Year from the date of supply of the equipment or part. The guarantee warrants replacing part against any Manufacturing Defect.

- The Bidder is expected to examine all instructions, forms, terms & conditions and specifications stated in the Bid Documents. Failure to furnish all information required in the Bid Document or submission of a Bid not substantially responding to the Bid Documents in every respect will be at the Bidder’s risk and may result in the rejection of the Bid. The following sections of the Bid Documents must be completed and submitted by the Bidder.

- SITE CONDITION: Before quoting, the contractor must visit the site to inspect the work and shall fully acquaint himself about the conditions and scope of work with regards to accessibility of site required for the satisfactory execution of work. Along with site visit certificate No compensation on account of any site difficulties will be entertained, at a later date, after award of the works.

Responsibility of bidder:

- Bidder shall facilitate his own manpower, equipment’s and tools to conduct the work.

- Ensure safety of the material and property of the institute, during the works.

- After service work any type emergences fault attend on call durations of one year.

Description of Work:

Air Circuit Breaker (ACB):

- Cleaning of breaker with CRC-226

- Removal of old Grease and re-greasing the same with recommended grease

- Check condition of arcing contact and gap between fixed and moving arcing contracts shall be checked.

- Check condition of arcing contact and gap between fixed and moving arcing contracts shall be checked.

- Checking the reset mechanism, tripping of breaker through push button.

- Checking tripping of ACB through protection release.

- Checking presence and proper tightening of hardware.

- Checking condition and alignment of jaw contract with cradle terminals

- Checking condition of ACB wiring and replace if required.

- Checking and adjusting gap between hylam sheet and side plate.

- Checking proper closing of all poles together.

- Checking working of anti-pumping device in case of EDO ACB.

- Checking alignment of SIC and its operation.

- Checking scrapping earth alignment.

- Checking condition of arc chutes.

- Checking U/V release pickup and drop off.

- Checking ACB tripping through Shunt release.

- Checking motor operation in case of EDO ACB.

- Checking closing coil operation in case of EDO ACB.

- Checking continuity and proper changeover of aux contract block.

- Checking IR between phases – phase (ACB Closed condition).

- Checking IR between phases – earth (ACB closed Condition).

- Checking IR between phases – earth (ACB in open condition).

- Setting of release as per the load.

- After the inspection, the ACB shall be checked for proper termination by MV drop Test.

- Checking condition of additional panel protection relays with secondary current injection test kit.

Vacuum Circuit Breaker (VCB):

- Cleaning of Vacuum Circuit Breaker with CRC-226

- Removal of old grease and re-greasing the same with recommended grease

- Check condition of SIC Contacts

- Checking condition and alignment of jaw Contact

- Checking and proper tightening of hardware

- Checking proper closing of all poles together

- Checking of breaker tripping through push button

- Checking and adjusting gap between hylam sheet and side plate

- Checking motor operation in case of EDO.

- Checking of auxiliary contacts continuity proper change over

- Checking presence of all circlips

- Checking IR between phase – phase (VCB closed condition)

- Checking IR between phase – earth (VCB closed condition)

- Checking IR between phase – earth (VCB in Open condition)

- Any faculty spare replace by new one, which will be charged extra.

LT / HT Panel& Capacitor Panel:

- Check condition of Bus bars

- Checking condition and alignment of jaw Contact

- Checking and proper tightening of hardware’s

- Checking of ad on block NO NC Point

- Checking of Thimble Tightness

- Checking of MCCB, MCB or other equipments and meters

Control Wiring:

- Checking of All Control Wiring

- Checking of Contactor in NO/NC Point

- Checking of Glass Relay in NO/NC Point

- Checking of MCCB, MCB or other equipments and meter terminals

- Checking of Contactor Coil Resistance

- Checking of auxiliary Contact

- Checking of indicator of Panel

- Checking selectors switch in NO/NC Point

- Checking of TNC Switch in NO/NC Point

Transformer:

- The oil level in oil cap under silica gel breather must be checked. If it is found the transformer oil inside the cup comes below the specified level, oil to be top up as per specified level.

- Color of silica gel in breather to be checked. If silica gel becomes pinkish, it should be replaced.

- The pockets for OTI, WTI (Oil Temperature Indicator & Winding Temperature Indicator) on the transformer top cover to be checked and if required oil to be replenished.

- Oil condition of OLTC to be examined. For that, oil sample to be taken from drain valve of diverter tank, and this collected oil sample to be tested for dielectric strength (BDV) and moisture content (PPM). If BDV is low and PPM for moisture is found high compared to recommend values, the oil inside the OLTC to be filtered and dehydrated.

- Mechanical inspection of Buchholz relays.

- All illumination, space heaters, to be checked whether they are functioning properly or not. If not, required maintenance action to be taken. All the terminal connections ofcontrol and relay wiring to be checked and tighten.

- The proper function of Pressure Release Device and Buchholz relay must be checked. For that, trip contacts and alarm contacts of the said devices are shorted by a small piece of wire, and observe whether the concerned relays in remote panel are properly working or not.

- Insulation resistanceof transformer must be checked with battery operated megger of appropriate KV range.

- The calibration of OTI and WTI.

Technical specification of equipment

| S. No. | Particulars | Technical Specification of equipment | UOM | Qty. |
| --- | --- | --- | --- | --- |
| A | Servicing of transformer |  |  |  |
| 1 | Servicing works for Transformers | 1000 kVA, 11/0.415 kV Transformer (CG) | Nos. | 3 |
| 2 | Oil testing | 1000 kVA, 11/0.415 kV Transformer (CG) | Nos. | 3 |
| 3 | Oil filtration & dehydration | 1001 kVA, 11/0.415 kV Transformer (CG) | Nos. | 3 |
| 4 | Top-up of transformer oil | 1002 kVA, 11/0.415 kV Transformer (CG) | Ltrs. | As Required (250 ) |
| 5 | Changing of Oil seals and gaskets (HT Side) | 1003 kVA, 11/0.415 kV Transformer (CG) | Nos. | 2 |
| 6 | Changing of Oil seals and gaskets (LT Side) | 1004 kVA, 11/0.415 kV Transformer (CG) | Nos. | 2 |
| B | Servicing works for Sub-Station equipment’s |  |  |  |
| 1 | Air Circuit Breakers (LT) | LT ACB (Make: L&T/Legrand) | Nos. | 19 |
| 2 | Vacuum Circuit Breakers (HT) | HT VCB (Make: ABB/CG) | Nos. | 4 |
| C | Servicing works for LT/HT Panel and Capacitor Panel |  |  |  |
| 1 | Servicing and cleaning work |  | LS | 3 |
| D | Supply of spares & material for servicing |  |  |  |
| 1 | ACB Front Facia Cover | L&T make. | Nos. | 2 |
| 2 | Under voltage release 415 Volt AC | L&T make. | Nos. | 4 |
| 3 | Mechanical key lock (LM)/ panel lock | L&T make. | Nos. | 20 |
| 4 | Shut Release Coil 240 V AC | L&T make. | Nos. | 4 |
| 5 | Control fuses 6 Amp. |  | Nos. | 5 |
| 6. | ACB release (O/L,S/T,GF) SR 18G | Make-L&T | Nos. | 1 |
| 7 | Arching moving contact | Make –L&T | Nos. | 4 |
| 8. | Arching fix contact (1000S1) | Make _ L&T | Nos. | 4 |
| 9 | Arc Chute (1000S1) | Make _ L&T | Nos. | 4 |
| 10 | Power Pack for VCB Panel 24 v DC output | Battery Exide | Nos. | 01 |
| 11 | ROM direct for MCCB upto 200A 36KA | Make _ L&T | Nos. | 3 |
| 12 | Closing Coil | L&T make | Nos. | 2 |
| 13 | Dig. MFM Meters Kwh.volt,amp,pf with RS485 | make- Schneider | Nos. | 5 |
| 6 | LED Panel indicator (Outgoing Feeders ) |  |  |  |
| a | Red | L&T make. | Nos. | 60 |
| b | Yellow | L&T make. | Nos. | 50 |
| c | Blue | L&T make. | Nos. | 50 |
| d | Green | L&T make | Nos. | 20 |
| 7 | Capacitor |  |  |  |
| a | Capacitor, 5 kVAR | L&T, (LTCC-D) | Nos. | 6 |
| b | Capacitor, 10 kVAR | L&T, (LTCC-D) | Nos. | 6 |
| c | Capacitor, 15 kVAR | L&T, (LTCC-D) | Nos. | 6 |
| d | Capacitor, 25 kVAR | L&T, (LTCC-D) | Nos. | 6 |
| 8 | MCB 4P 6 AMP | L&T | Nos. | 18 |
| 9 | Wring and thimbles etc. Miscellaneous(Hardware, Wire, Lugs, Pvc Channel , Mcb Chanel, Connectors,Netural Links , Sprial , Saddle & Packing Material ) |  | Set. | 15 |
| 10 | Main LT Panel with Servicing Clanging and hardware (Non domestic power supply panel ) |  | Job | 1 |
| 11 | Main LT Panel with Servicing Clanging and hardware (Domestic power supply panel) |  |  |  |
| 12 | DG Alternator Service |  | Nos. | 3 |
| 13 | Earthing Testing |  | Nos. | 40 |
| 14 | Silica gel |  | Kg | 6 |

Commercial Bid: (in separate sealed envelope)

Servicing of LT & HT Panel, VCB, ACB, Capacitor Bank, DG Set Alternator Earthing Testing and Transformers

| S. No. | Particulars | Technical Specification of equipment | UOM | Qty. | Rate | Amount |
| --- | --- | --- | --- | --- | --- | --- |
| A | Servicing of transformer |  |  |  |  |  |
| 1 | Servicing works for Transformers | 1000 kVA, 11/0.415 kV Transformer (CG) | Nos. | 3 |  |  |
| 2 | Oil testing | 1000 kVA, 11/0.415 kV Transformer (CG) | Nos. | 3 |  |  |
| 3 | Oil filtration & dehydration | 1001 kVA, 11/0.415 kV Transformer (CG) | Nos. | 3 |  |  |
| 4 | Top-up of transformer oil | 1002 kVA, 11/0.415 kV Transformer (CG) | Ltrs. | As Required (250 ) |  |  |
| 5 | Changing of Oil seals and gaskets (HT Side) | 1003 kVA, 11/0.415 kV Transformer (CG) | Nos. | 2 |  |  |
| 6 | Changing of Oil seals and gaskets (LT Side) | 1004 kVA, 11/0.415 kV Transformer (CG) | Nos. | 2 |  |  |
| B | Servicing works for Sub-Station equipment’s |  |  |  |  |  |
| 1 | Air Circuit Breakers (LT) | LT ACB (Make: L&T/Legrand) | Nos. | 19 |  |  |
| 2 | Vacuum Circuit Breakers (HT) | HT VCB (Make: ABB/CG) | Nos. | 4 |  |  |
| C | Servicing works for LT/HT Panel and Capacitor Panel |  |  |  |  |  |
| 1 | Servicing and cleaning work |  | LS | 3 |  |  |
| D | Supply of spares & material for servicing |  |  |  |  |  |
| 1 | ACB Front Facia Cover | L&T make. | Nos. | 2 |  |  |
| 2 | Under voltage release 415 Volt AC | L&T make. | Nos. | 4 |  |  |
| 3 | Mechanical key lock (LM)/ panel lock | L&T make. | Nos. | 20 |  |  |
| 4 | Shut Release Coil 240 V AC | L&T make. | Nos. | 4 |  |  |
| 5 | Control fuses 6 Amp. |  | Nos. | 5 |  |  |
| 6. | ACB release (O/L,S/T,GF) SR 18G | Make-L&T | Nos. | 1 |  |  |
| 7 | Arching moving contact | Make –L&T | Nos. | 4 |  |  |
| 8. | Arching fix contact (1000S1) | Make _ L&T | Nos. | 4 |  |  |
| 9 | Arc Chute (1000S1) | Make _ L&T | Nos. | 4 |  |  |
| 10 | Power Pack for VCB Panel 24 v DC output | Battery Exide | Nos. | 01 |  |  |
| 11 | ROM direct for MCCB upto 200A 36KA | Make _ L&T | Nos. | 3 |  |  |
| 12 | Closing Coil | L&T make | Nos. | 2 |  |  |
| 13 | Dig. MFM Meters Kwh.volt,amp,pf with RS485 | make- Schneider | Nos. | 5 |  |  |
| 6 | LED Panel indicator (Outgoing Feeders ) |  |  |  |  |  |
| a | Red | L&T make. | Nos. | 60 |  |  |
| b | Yellow | L&T make. | Nos. | 50 |  |  |
| c | Blue | L&T make. | Nos. | 50 |  |  |
| d | Green | L&T make | Nos. | 20 |  |  |
| 7 | Capacitor |  |  |  |  |  |
| a | Capacitor, 5 kVAR | L&T, (LTCC-D) | Nos. | 6 |  |  |
| b | Capacitor, 10 kVAR | L&T, (LTCC-D) | Nos. | 6 |  |  |
| c | Capacitor, 15 kVAR | L&T, (LTCC-D) | Nos. | 6 |  |  |
| d | Capacitor, 25 kVAR | L&T, (LTCC-D) | Nos. | 6 |  |  |
| 8 | MCB 4P 6 AMP | L&T | Nos. | 18 |  |  |
| 9 | Wring and thimbles etc. Miscellanous(Hardware, Wire, Lugs, Pvc Channel , Mcb Chanel, Connectors,Netural Links , Sprial , Saddle & Packing Material ) |  | Set. | 15 |  |  |
| 10 | Main LT Panel with Servicing Clanging and hardware (Non domestic power supply panel ) |  | Job | 1 |  |  |
| 11 | Main LT Panel with Servicing Clanging and hardware (Domestic power supply panel) |  |  |  |  |  |
| 12 | DG Alternator Service |  | Nos. | 3 |  |  |
| 13 | Earthing Testing |  | Nos. | 40 |  |  |
| 14 | Silica gel |  | Kg | 6 |  |  |

| Total |  |
| --- | --- |
| GST |  |
| Total including GST |  |

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should be including all (Packing, forwarding, Transit Insurance, Transportation Loading/unloading, and Installation etc.). Loading/unloading up to 50 Mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- Bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

All charges applicable shall be clearly mentioned with the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

Signature with seal