The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “Supply and installation CN-CS-1600 S1 4 Pole Air Circuit Breaker (Related Current 1600 Amp Brand L&T)”.  Bidders can submit their sealed offer/s at the following address by Speed-Post/ Registered Post/ By-hand (but not by Courier)/ before 05:00 PM on 05.03.2023.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the Institute after marking due entries.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Email: directoroffice@lnmiit.ac.in

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory are required to be submitted in two separate envelopes/files. Both envelopes/files should be duly marked as “Technical bid Supply and installation CN-CS-1600 S1 4 Pole Air Circuit Breaker (Related Current 1600 Amp Brand L&T)” and “Commercial Bid for Supply and installation CN-CS-1600 S1 4 Pole Air Circuit Breaker (Related Current 1600 Amp Brand L&T)” respectively. Both Envelopes shall be enclosed in a single envelope bearing the heading “Bid for Supply and installation CN-CS-1600 S1 4 Pole Air Circuit Breaker (Related Current 1600 Amp Brand L&T)”. Bids are liable to be rejected if any or both of the technical or commercial offers are found in open condition or required information is not found with the offer.

Technical Bid: (in a separate sealed envelope)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turn over for the last three years to be mentioned. (Copy to be enclosed)

- List of the client to whom the vendor has delivered the goods or provided the services in past.

- Specification as mentioned below, shall be provided as per the details given below:

Scope of work, Technical data sheet and Specification of the item/s

Name of Work

Supply and installation CN-CS-1600 S1 4 Pole Air Circuit Breaker (Related Current 1600 Amp Brand L&T)

Scope of work

| Technical Specifications_ CN-CS 1600S1 Air Circuit Breakers |  |  |  |  |
| --- | --- | --- | --- | --- |
| S.NO. | DESCRIPTION OF ITEM |  | UNIT | Qty. |
|  | SUPPLY & INSTALLATION OF VCB |  |  |  |
|  | SUB-STATION LT SIDE WORKS |  | Set | 1 |
| A | L.T. PANELS |  |  |  |
|  | Supplying, erection and commissioning of following totally enclosed cubical type compartmentalized, indoor mounting free standing, front operated, front access dust and vermin proof, (Ingress protection IP 42) switchboards fabricated from 2mm thick CRCA sheets with hinged, gasketted and lockable doors including the cost of powder coating of approved shade of minimum 50 microns film thickness on MS surface cleaned and prepared with 7 tank process and including the cost of interconnections, heavy duty aluminum crimping lugs, bonding to earth suitable for a fault level of 25 MVA symmetrical at 415 volts, including connecting to exisiting LT panel via aluminum bus bars of suitable size. |  |  |  |
|  | All switchboards shall have provision for entry of cables from the top or bottom as required. |  |  |  |
|  | All live accessible parts shall have provision for entry of cables from the top or bottom as required. |  |  |  |
|  | All live accessible parts shall be shrouded and all equipment shall be finger touch proof. The busbars insulation shall be with heat shrinkable sleeves. SMC / DMC shrouds and busbar supports shall be used. Padlocking facility shall be provided on all outgoing feeders’ doors and switch handles shall be lockable in OFF position. |  |  |  |
|  | All kA rating indicated figures are Ics value |  |  |  |
| a.1 | Bus Coupler LT PANEL |  |  |  |
|  | 1 No. 1600A, 4 pole Microprocessor based motorized draw out type ACB (50 KA) with U/V, shunt release, with a minimum of 6 NO & 6 NC Auxiliary contacts.( Rated Current : 1600 Amp, Brand : L&T, Breaking Capacity : 50 KV, Phase : 3, Rated Voltag : 415 V AC, Power Source : Electrical) |  |  |  |
|  | Rating (A) | 1600 |  |  |
|  | Type Designation | S1 |  |  |
|  | Rated current (A) at 50°C In | 1600 |  |  |
|  | Rated operational voltage (V), 50/60Hz Ue | 415 |  |  |
|  | Rated insulation voltage (V), 50/60Hz U | 1000 |  |  |
|  | No. of poles | 4P |  |  |
|  | Rated ultimate short circuit breaking capacity 50/60Hz (kA rms) Icu (380/415/500V) | 50 |  |  |
|  | Rated service short circuit breaking capacity 50/60Hz (kA rms) Ics (380/415/500V) | 50 |  |  |
|  | Rated short time withstand capacity 50/60Hz (kA rms) Icw (0.5 sec) | 50 |  |  |
|  | Rated making capacity 50/60Hz (kA peak) Icm (380/415/500V) | 50 |  |  |
|  | Rated impulse withstand voltage of main circuit (kV) Uimp | 12 |  |  |
|  | Rated impulse withstand voltage of aux. circuit (kV) Uimp | 4 |  |  |
|  | Typical opening time (ms) | 60 |  |  |
|  | Typical closing time (ms | 40 |  |  |
|  | Utilization category | B |  |  |
|  | Electrical & Mechanical life (operating cycles) | 20000 |  |  |
|  | Electrical life without maintenance | 7000 |  |  |
|  | Draw out 4 Pole |  |  |  |
|  | PROTECTION RELEASES SR 18G |  |  |  |
|  | Microprocessor Based Release - SR18G |  |  |  |
|  | Salient Features |  |  |  |
|  | self –powered &True RMS sensing |  |  |  |
|  | True Hot & Cold characteristics & switchable Thermal Memory |  |  |  |
|  | Offers comprehensive protection against Overload - Phase & Neutral, Short-Circuit, Instantaneous, Earth Fault |  |  |  |
|  | Settable Overload delay |  |  |  |
|  | Settable Instantaneous setting with provision of “OFF” |  |  |  |
|  | I t ON/OFF for Short-Circuit and Earth Fault protection |  |  |  |
|  | individual Fault LED indication |  |  |  |
|  | Provision for Self-diagnostic test |  |  |  |
|  | Conformance to EMI/EMC standards |  |  |  |
|  | Testing through Universal Test kit |  |  |  |
|  | Type of Protection | Pick-up current |  |  |
|  | Overload (Phase) | Ir - 0.4 to 1.0 times In Steps :0.40, 0.50, 0.60, 0.70, 0.75, 0.80, 0.85, 0.90, 0.95, 1 |  |  |
|  | Overload (Neutral) | In - 50% to 200% times Ir Steps : 50%, 100%, 150%, 200% |  |  |
|  | Short-Circui | 2 to 10 times In Steps : 2, 3, 4, 5, 6, 7, 8, 9, 10 |  |  |
|  | Instantaneous | 2 to 16 times In Steps : 2, 3, 4, 6, 8, 10, 12, 14, 16, OFF |  |  |
|  | Earth fault* | 0.2 to 0.6 times In Steps : 0.2, 0.3, 0.4, 0.5, 0.6 |  |  |
|  | In 3 phase, 4 wire system, Neutral CT is required for earth fault protection |  |  |  |
|  | INDICATING PANEL |  |  |  |
|  | Incomer shall have the following indicating panel. |  |  |  |
|  | 96mm sq. flush voltmeter scaled 0-500 volt with 3 way and OFF selector switch. |  |  |  |
|  | Three nos. 1600/5 class 1.0 accuracy 15 BA burden C.T.s for metering. |  |  |  |
|  | 96 mm square flush ammeter scaled 0-1000 amps with 3 way and OFF selector switch. |  |  |  |
|  | Three phase indicating lights. |  |  |  |
|  | 1 Set O/V,O/C, E/F relay numerical |  |  |  |
| a.2 | Bus Bar |  |  |  |
|  | 1600A TPN aluminum Bus Bars with heat shrinkable colored insulated PVC sleeves. |  |  |  |
| a.3 | ELECTRICAL INTERLOCKING |  |  |  |
|  | Electrical interlocking of all sources and bus couplers, including providing & fixing of UV-Shunt relays, auxiliary contacts, control wiring, MCB's for control wiring, etc. as per requirement complete. |  |  |  |
| 2 | Supplying and making end termination with double compression, brass compression gland including providing and crimping with aluminum solder less lugs/ ferrules for XLPE insulated armored power aluminum conductor cable of 1.1 KV grade as required. |  |  |  |
| a) | 3-5 x 300 sq.mm |  | Each | 18 |
| B | Miscellaneous |  |  |  |
| 1 | Providing and laying 250 mm dia Class III uPVC pipe, after cutting and dismantling of PCC and digging upto the level upto existing trench in Sub-Station, and back filling, repairing and making good as required, for laying of LT cable from DG foundation to LT Panel in Sub-Station. |  | Meter | 20 |
| 2 | Supply and installation of 1000 mm wide 25 mm thick rubber matting of approved make as per electricity rules .(LT Side) |  | Meter | 10 |
| 3 | Supplying & Grounding Maintance free chemical filled earthing electrode 48mm x 3000mm including accessories & providing masonry enclosure with cover plate locking arrangement complete as required. |  | Set | 2 |
| 4 | Providing, laying in ground and on surface with saddles at required intervals and testing of 25 X 6 mm size of GI strip, including jointing of GI strips with Nuts and Bolts at required locations. |  | Meter | 25 |
| 5 | Providing and fixing PVC shrinkable sleeve of required size for GI strip of size 25 X 6 mm, for earting strips from Transformer to Pit. |  | Meter | 100 |
| 6 | Supply and installation of 1000 mm wide 25 mm thick rubber matting of approved make as per electricity rules .(HT Side) |  | Meter | 2 |

Commercial Bid: (in separate sealed envelope)

Supply and installation CN-CS-1600 S1 4 Pole Air Circuit Breaker (Related Current 1600 Amp Brand L&T)

| Technical Specifications_ CN-CS 1600S1 Air Circuit Breakers |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| S.NO. | DESCRIPTION OF ITEM |  | UNIT | Qty. | Rate | Amount |  |
|  | SUPPLY & INSTALLATION OF VCB |  |  |  |  |  |  |
|  | SUB-STATION LT SIDE WORKS |  | Set | 1 |  |  |
| A | L.T. PANELS |  |  |  |  |  |
|  | Supplying, erection and commissioning of following totally enclosed cubical type compartmentalized, indoor mounting free standing, front operated, front access dust and vermin proof, (Ingress protection IP 42) switchboards fabricated from 2mm thick CRCA sheets with hinged, gasketted and lockable doors including the cost of powder coating of approved shade of minimum 50 microns film thickness on MS surface cleaned and prepared with 7 tank process and including the cost of interconnections, heavy duty aluminum crimping lugs, bonding to earth suitable for a fault level of 25 MVA symmetrical at 415 volts, including connecting to exisiting LT panel via aluminum bus bars of suitable size. |  |  |  |  |  |
|  | All switchboards shall have provision for entry of cables from the top or bottom as required. |  |  |  |  |  |
|  | All live accessible parts shall have provision for entry of cables from the top or bottom as required. |  |  |  |  |  |
|  | All live accessible parts shall be shrouded and all equipment shall be finger touch proof. The busbars insulation shall be with heat shrinkable sleeves. SMC / DMC shrouds and busbar supports shall be used. Padlocking facility shall be provided on all outgoing feeders doors and switch handles shall be lockable in OFF position. |  |  |  |  |  |
|  | All kA rating indicated figures are Ics value |  |  |  |  |  |
| a.1 | Bus Coupler LT PANEL |  |  |  |  |  |
|  | 1 No. 1600A, 4 pole Microprocessor based motorized draw out type ACB (50 KA) with U/V, shunt release, with a minimum of 6 NO & 6 NC Auxiliary contacts.( Rated Current : 1600 Amp, Brand : L&T, Breaking Capacity : 50 KV, Phase : 3, Rated Voltag : 415 V AC, Power Source : Electrical) |  |  |  |  |  |
|  | Rating (A) | 1600 |  |  |  |  |
|  | Type Designation | S1 |  |  |  |  |
|  | Rated current (A) at 50°C In | 1600 |  |  |  |  |
|  | Rated operational voltage (V), 50/60Hz Ue | 415 |  |  |  |  |
|  | Rated insulation voltage (V), 50/60Hz U | 1000 |  |  |  |  |
|  | No. of poles | 4P |  |  |  |  |
|  | Rated ultimate short circuit breaking capacity 50/60Hz (kA rms) Icu (380/415/500V) | 50 |  |  |  |  |
|  | Rated service short circuit breaking capacity 50/60Hz (kA rms) Ics (380/415/500V) | 50 |  |  |  |  |
|  | Rated short time withstand capacity 50/60Hz (kA rms) Icw (0.5 sec) | 50 |  |  |  |  |
|  | Rated making capacity 50/60Hz (kA peak) Icm (380/415/500V) | 50 |  |  |  |  |
|  | Rated impulse withstand voltage of main circuit (kV) Uimp | 12 |  |  |  |  |
|  | Rated impulse withstand voltage of aux. circuit (kV) Uimp | 4 |  |  |  |  |
|  | Typical opening time (ms) | 60 |  |  |  |  |
|  | Typical closing time (ms | 40 |  |  |  |  |
|  | Utilization category | B |  |  |  |  |
|  | Electrical & Mechanical life (operating cycles) | 20000 |  |  |  |  |
|  | Electrical life without maintenance | 7000 |  |  |  |  |
|  | Draw out 4 Pole |  |  |  |  |  |
|  | PROTECTION RELEASES SR 18G |  |  |  |  |  |
|  | Microprocessor Based Release - SR18G |  |  |  |  |  |
|  | Salient Features |  |  |  |  |  |
|  | self –powered &True RMS sensing |  |  |  |  |  |
|  | True Hot & Cold characteristics & switchable Thermal Memory |  |  |  |  |  |
|  | Offers comprehensive protection against Overload - Phase & Neutral, Short-Circuit, Instantaneous, Earth Fault |  |  |  |  |  |
|  | Settable Overload delay |  |  |  |  |  |
|  | Settable Instantaneous setting with provision of “OFF” |  |  |  |  |  |
|  | I t ON/OFF for Short-Circuit and Earth Fault protection |  |  |  |  |  |
|  | individual Fault LED indication |  |  |  |  |  |
|  | Provision for Self-diagnostic test |  |  |  |  |  |
|  | Conformance to EMI/EMC standards |  |  |  |  |  |
|  | Testing through Universal Test kit |  |  |  |  |  |
|  | Type of Protection | Pick-up current |  |  |  |  |
|  | Overload (Phase) | Ir - 0.4 to 1.0 times In Steps :0.40, 0.50, 0.60, 0.70, 0.75, 0.80, 0.85, 0.90, 0.95, 1 |  |  |  |  |
|  | Overload (Neutral) | In - 50% to 200% times Ir Steps : 50%, 100%, 150%, 200% |  |  |  |  |
|  | Short-Circui | 2 to 10 times In Steps : 2, 3, 4, 5, 6, 7, 8, 9, 10 |  |  |  |  |
|  | Instantaneous | 2 to 16 times In Steps : 2, 3, 4, 6, 8, 10, 12, 14, 16, OFF |  |  |  |  |
|  | Earth fault* | 0.2 to 0.6 times In Steps : 0.2, 0.3, 0.4, 0.5, 0.6 |  |  |  |  |
|  | In 3 phase, 4 wire system, Neutral CT is required for earth fault protection |  |  |  |  |  |
|  | INDICATING PANEL |  |  |  |  |  |
|  | Incomer shall have the following indicating panel. |  |  |  |  |  |
|  | 96mm sq. flush voltmeter scaled 0-500 volt with 3 way and OFF selector switch. |  |  |  |  |  |
|  | Three nos. 1600/5 class 1.0 accuracy 15 BA burden C.T.s for metering. |  |  |  |  |  |
|  | 96 mm square flush ammeter scaled 0-1000 amps with 3 way and OFF selector switch. |  |  |  |  |  |
|  | Three phase indicating lights. |  |  |  |  |  |
|  | 1 Set O/V,O/C, E/F relay numerical |  |  |  |  |  |
| a.2 | Bus Bar |  |  |  |  |  |
|  | 1600A TPN aluminum Bus Bars with heat shrinkable colored insulated PVC sleeves. |  |  |  |  |  |
| a.3 | ELECTRICAL INTERLOCKING |  |  |  |  |  |
|  | Electrical interlocking of all sources and bus couplers, including providing & fixing of UV-Shunt relays, auxiliary contacts, control wiring, MCB's for control wiring, etc. as per requirement complete. |  |  |  |  |  |
| 2 | Supplying and making end termination with double compression, brass compression gland including providing and crimping with aluminum solder less lugs/ ferrules for XLPE insulated armored power aluminum conductor cable of 1.1 KV grade as required. |  |  |  |  |  |
| a) | 3-5 x 300 sq.mm |  | Each | 18 |  |  |
| B | Miscellaneous |  |  |  |  |  |
| 1 | Providing and laying 250 mm dia Class III uPVC pipe, after cutting and dismantling of PCC and digging upto the level upto existing trench in Sub-Station, and back filling, repairing and making good as required, for laying of LT cable from DG foundation to LT Panel in Sub-Station. |  | Meter | 20 |  |  |
| 2 | Supply and installation of 1000 mm wide 25 mm thick rubber matting of approved make as per electricity rules .(LT Side) |  | Meter | 10 |  |  |
| 3 | Supplying & Grounding Maintance free chemical filled earthing electrode 48mm x 3000mm including accessories & providing masonry enclosure with cover plate locking arrangement complete as required. |  | Set | 2 |  |  |
| 4 | Providing, laying in ground and on surface with saddles at required intervals and testing of 25 X 6 mm size of GI strip, including jointing of GI strips with Nuts and Bolts at required locations. |  | Meter | 25 |  |  |
| 5 | Providing and fixing PVC shrinkable sleeve of required size for GI strip of size 25 X 6 mm, for earting strips from Transformer to Pit. |  | Meter | 100 |  |  |
| 6 | Supply and installation of 1000 mm wide 25 mm thick rubber matting of approved make as per electricity rules .(HT Side) |  | Meter | 2 |  |  |
| Total |  |  |  |  |  |  |
| GST |  |  |  |  |  |  |
| Total including GST |  |  |  |  |  |  |

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should be including all (Packing, forwarding, Transit Insurance, Transportation Loading/unloading, Installation etc.). Loading/unloading up to 50 Mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- Bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

All charges applicable shall be clearly mentioned with the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

Signature with seal