The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “Supply and installation of Feeder Panel with 3.5 x 95 sqmm XLPE Insulated armoured Al. Conductor Power cable of 1.1 KV Grade (Make Polycab/KEI/RR/Apar)”.  Bidders can submit their sealed offer/s at the following address by Speed-Post/ Registered Post/ By-hand (but not by Courier)/ before 05:00 PM on 05.03.2023.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the Institute after marking due entries.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Email: directoroffice@lnmiit.ac.in

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory are required to be submitted in two separate envelopes/files. Both envelopes/files should be duly marked as “Technical bid for the Supply and installation of Feeder Panel with 3.5 x 95 sqmm XLPE Insulated armoured Al. Conductor Power cable of 1.1 KV Grade (Make Polycab/KEI/RR/Apar)” and “Commercial Bid for Supply and installation of Feeder Panel with 3.5 x 95 sqmm XLPE Insulated armoured Al. Conductor Power cable of 1.1 KV Grade (Make Polycab/KEI/RR/Apar)” respectively. Both Envelopes shall be enclosed in a single envelope bearing the heading “Bid for Supply and installation of Feeder Panel with 3.5 x 95 sqmm XLPE Insulated armoured Al. Conductor Power cable of 1.1 KV Grade (Make Polycab/KEI/RR/Apar)”. Bids are liable to be rejected if any or both of the technical or commercial offers are found in open condition or required information is not found with the offer.

Technical Bid: (in a separate sealed envelope)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turn over for the last three years to be mentioned. (Copy to be enclosed)

- List of the client to whom the vendor has delivered the goods or provided the services in past.

- Specification as mentioned below, shall be provided as per the details given below:

Scope of work, Technical data sheet and Specification of the item/s

Name of Work

Supply and installation of Feeder Panel with 3.5 x 95 sqmm XLPE Insulated armoured Al. Conductor Power cable of 1.1 KV Grade (Make Polycab/KEI/RR/Apar)

| S.NO. | DESCRIPTION OF ITEM | UNIT | Quantity |
| --- | --- | --- | --- |
| A | L.T. CABLES XLPE (Substation to Guest House ) |  |  |
| 1 | Supplying of following sizes of XLPE insulated armored aluminum conductor power cable of 1.1 KV grade. |  |  |
| a | 3-5 x 95 sq.mm | Meter | 1500 |
| 2 | Laying and fixing of XLPE insulated Aluminum Conductor Armored Cables of 1.1 KV grade of following size on ground/ cable tray / surface mounted along with misc. accessories like Cable Ties / Saddles / Cable Tags etc. |  |  |
| a | 3-5 x 95 sq.mm | Meter | 1500 |
| 3 | Digging and back filling 450mm / 600 mm wide and 750 mm deep trench for laying cable for LT cables as required along with sand and brick lining as per IS specification. | Meter | 500 |
| 4 | Supplying and making end termination with double compression, brass compression gland including providing and crimping with aluminum solder less lugs/ ferrules for XLPE insulated armored power aluminum conductor cable of 1.1 KV grade as required. |  |  |
| a | 3-5 x 300 sq.mm | Nos. | 6 |
| b | 3-5 x 95 sq.mm | Nos. | 8 |
| B | External Feeder Panels |  |  |
|  | Feeder Pillars |  |  |
|  | Supply, installation, testing and commissioning of cubicle type, LT outdoor feeder pillar, double door fully compartmentalized, dust and vermin proof, made out of 2 m.m. thick CRCA sheet steel, floor mounted, free standing, lockable, confirming to IP- 54, mounted on finished brick foundation, powder coated/ epoxy painted, cable entry from bottom, with following configuration- (FP) |  |  |
|  | F.P - HVAC |  |  |
|  | INCOMER |  |  |
|  | 630 A 4P MCCB - 1 No. |  |  |
|  | 1000 A, TPN Aluminum bus bar. |  |  |
|  | 50 x10 sq. m.m. Aluminum earth bus. |  |  |
|  | OUTGOING |  |  |
|  | 63 A 4P MCCB - 8 Nos. |  |  |
|  | 200 A 4P MCCB - 2 Nos. |  |  |
|  | 320 A 4P MCCB - 2 Nos. |  |  |
|  | Suitable cable gland for 3.5Cx 300 sq. mm. | Set | 1 |
| C | EARTHING |  |  |
| 1 | Supplying & Grounding Maintance free chemical filled earthing electrode 48mm x 3000mm including accessories & providing masonry enclosure with cover plate locking arrangement complete as required. | Set | 4 |
| 2 | Providing and laying GI strip 25 mm x 6 mm in recess for connection etc. as required. | Meter | 100 |

Commercial Bid: (in separate sealed envelope)

Supply and installation of Feeder Panel with 3.5 x 95 sqmm XLPE Insulated armoured Al. Conductor Power cable of 1.1 KV Grade (Make Polycab/KEI/RR/Apar)

| "HVAC Feeder Penel & Cabling Work For Substation to Guest house" |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| S.NO. | DESCRIPTION OF ITEM | UNIT | Quantity | Rate | Amount |
| A | L.T. CABLES XLPE (Substation to Guest House ) |  |  |  |  |
| 1 | Supplying of following sizes of XLPE insulated armored aluminum conductor power cable of 1.1 KV grade. |  |  |  |  |
| a | 3-5 x 95 sq.mm | Meter | 1500 |  |  |
| 2 | Laying and fixing of XLPE insulated Aluminum Conductor Armored Cables of 1.1 KV grade of following size on ground/ cable tray / surface mounted along with misc. accessories like Cable Ties / Saddles / Cable Tags etc. |  |  |  |  |
| a | 3-5 x 95 sq.mm | Meter | 1500 |  |  |
| 3 | Digging and back filling 450mm / 600 mm wide and 750 mm deep trench for laying cable for LT cables as required along with sand and brick lining as per IS specification. | Meter | 500 |  |  |
| 4 | Supplying and making end termination with double compression, brass compression gland including providing and crimping with aluminum solder less lugs/ ferrules for XLPE insulated armored power aluminum conductor cable of 1.1 KV grade as required. |  |  |  |  |
| a | 3-5 x 300 sq.mm | Nos. | 6 |  |  |
| b | 3-5 x 95 sq.mm | Nos. | 8 |  |  |
| B | External Feeder Panels |  |  |  |  |
|  | Feeder Pillars |  |  |  |  |
|  | Supply, installation, testing and commissioning of cubicle type, LT outdoor feeder pillar, double door fully compartmentalized, dust and vermin proof, made out of 2 m.m. thick CRCA sheet steel, floor mounted, free standing, lockable, confirming to IP- 54, mounted on finished brick foundation, powder coated/ epoxy painted, cable entry from bottom, with following configuration- (FP) |  |  |  |  |
|  | F.P - HVAC |  |  |  |  |
|  | INCOMER |  |  |  |  |
|  | 630 A 4P MCCB - 1 No. |  |  |  |  |
|  | 1000 A, TPN Aluminum bus bar. |  |  |  |  |
|  | 50 x10 sq. m.m. Aluminum earth bus. |  |  |  |  |
|  | OUTGOING |  |  |  |  |
|  | 63 A 4P MCCB - 8 Nos. |  |  |  |  |
|  | 200 A 4P MCCB - 2 Nos. |  |  |  |  |
|  | 320 A 4P MCCB - 2 Nos. |  |  |  |  |
|  | Suitable cable gland for 3.5Cx 300 sq. mm. | Set | 1 |  |  |
| C | EARTHING |  |  |  |  |
| 1 | Supplying & Grounding Maintance free chemical filled earthing electrode 48mm x 3000mm including accessories & providing masonry enclosure with cover plate locking arrangement complete as required. | Set | 4 |  |  |
| 2 | Providing and laying GI strip 25 mm x 6 mm in recess for connection etc. as required. | Meter | 100 |  |  |

| Total |  |
| --- | --- |
| GST |  |
| Total including GST |  |

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should be including all (Packing, forwarding, Transit Insurance, Transportation Loading/unloading, Installation etc.). Loading/unloading up to 50 Mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- Bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

All charges applicable shall be clearly mentioned with the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

Signature with seal