The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposal from competent vendors for “Supply and Installation of 1.5 TR Split Type 5 Star Air Conditioning with Power supply works for Boys Hostels 1, 2 & 3 in Warden Office”. Bidders can submit their sealed offer/s at the following address by Email/Speed-Post/ Registered Post/ By-hand (but not by Courier)/ before 05:00 PM on 05/03/2023.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the Institute after marking due entries.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Email: directoroffice@lnmiit.ac.in

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory are required to be submitted in two separate envelopes. Both envelopes should be duly marked as “Technical bid for “Supply and Installation of 1.5 TR Split Type 5 Star Air Conditioning with Power supply works for Boys Hostels 1, 2 & 3 in Warden Office” and “Commercial Bid for “Supply and Installation of 1.5 TR Split Type 5 Star Air Conditioning with Power supply works for Boys Hostels 1, 2 & 3 in Warden Office” respectively. Both Envelopes shall be enclosed in a single envelope bearing the heading “Bid for “Supply and Installation of 1.5 TR Split Type 5 Star Air Conditioning with Power supply works for Boys Hostels 1, 2 & 3 in Warden Office”. Bids are liable to be rejected if any or both of the technical or commercial offers are found in open condition or required information is not found with the offer.

Technical Bid: (in a separate sealed envelope)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turn over for the last three years to be mentioned. (Copy to be enclosed)

- List of the client to whom the vendor has delivered the goods or provided the services in past.

- Specification as mentioned below, shall be provided as per the details given below:

Scope of work, Technical data sheet and Specification of the item/s

Technical Specifications

1.5 TR Split 5 Star Inverter Supper Efficient Air Conditioner for Boys Hostels 1, 2 & 3 in Warden Office

| S No | PARTICULARS |  | UNIT | QTY |
| --- | --- | --- | --- | --- |
| A | Supply of Air conditioning system of following items |  |  |  |
|  | Supply of 1.5 TR 5 Star Split Air Conditioner with 1 year Standard Manufacturer Warranty and 5 Year compressor Warranty. White (Copper Condenser) 1.5 TR Split type air conditioning machine with 1 nos. indoor unit & 1 nos. 1.5 TR outdoor unit. Including all accessories. Preferred Makes: Hitachi / Daikin/Voltas/Carrier/EESL |  |  |  |
|  | Outdoor Unit 1.5TR |  |  |  |
|  | Outdoor condensing unit shall comprise of 1 nos. Rotary /reciprocating/ scroll compressor of 1.5 TR capacity. Air cooled condenser having copper tube with mechanically bonded aluminum fins of adequate heat transfer area as per manufacturer’s standard, complete with fan and fan motor of required capacity with independent circuit complete with interconnecting piping, wiring and controls. |  |  |  |
|  | Indoor Unit 1.5 TR |  |  |  |
|  | Indoor unit of 1.5 TR capacity, consisting of multi row cooling coil having copper tube with mechanically bonded aluminum fins, thermostat expansion valve, dynamically balanced centrifugal blower driven by TEFC squirrel cage induction motor, cleanable synthetic filter, insulated drain pan complete with microprocessor control for efficient operation, inter connecting copper tube duly insulated with nitrile rubber molded section and cordless hand set. |  |  |  |
|  | Technical Specifications |  |  |  |
|  | Description | Particulars |  |  |
|  | Cooling Capacity Full Load (100%) | 5280/1.5 W/TR |  |  |
|  | Cooling Power Full Load (100%) | 1310 Watt |  |  |
|  | Efficiency (Star Rating) | 5 star AC |  |  |
|  | Power Supply (V/Hz/PH) | 230/50/1 Phase |  |  |
|  | Air flow volume _indoor | 950 CMH |  |  |
|  | Noise Level_ Indoor | 46 dB(A) |  |  |
|  | Operation | LCD Remote |  |  |
|  | Wide operating voltage Range | 145-270 V |  |  |
|  | Max operating Ambient Temp Range | 52⁰ C |  |  |
|  | Refrigerant Gas | R32/410 |  |  |
|  | Connecting Pipe | Cu-Cu(12.5mm & 6.35mm) |  |  |
|  | Condenser Coil | Fin & Tube |  |  |
|  | Machine with 1 outdoor and 1 indoor units |  | Nos. | 3 |
| B | Supply and Installation of Air conditioning system of following items |  |  |  |
| 1 | Lifting, shifting, positioning, installation, testing and commissioning of outdoor units, fittings (Imported Y-joints & header etc.) remote controls of indoor units, including gas charging with R32/R410A gas as required, complete as per specification. pressure testing of concealed indoor units |  |  |  |
| a | Indoor Unit _ 1.5 TR |  | Nos | 3 |
| b | Outdoor Unit_ 1.5 TR |  | Nos. | 3 |
| 2 | Refrigerant Copper Piping |  |  |  |
|  | Interconnecting refrigerant pipe work with (12.5mm/6.35 mm thick) closed cell elastomeric nitrile rubber tubular insulation between each set of indoor & outdoor units as per specifications, all piping inside the room shall be properly supported with MS hanger. |  | meter | 60 |
| 3 | Drain Piping |  |  |  |
|  | Providing and fixing rigid PVC piping complete with fittings, supports as per specifications and duly insulated with 6 mm thick closed cell nitrile rubber insulation. |  |  |  |
| a | 25 mm dia ( Brand : Supreme/Kisan/AKG) |  | Meter | 30 |
| 4. | Providing and fixing of MS Wall/ floor mounted stand for outdoor unit |  | Nos. | 3 |
| 5 | Power and control cabling between indoor and outdoor / ac panel, HAT, etc. Make:-Polycab/KEI/RR/APAR) |  |  |  |
| 1 | 3 Core 2.5 sq mm cu flexible cable |  | Meter | 100 |
| 6 | Supply and installation of 4 core 4 sq mm copper armored cables DB to Panel. (Make:-Polycab/KEI/RR/APAR) |  | Meter | 200 |
| 7 | Supply and installation of Single Door, MS Powder coated Single phase 8 way Distribution board, with all accessories. |  | Nos. | 3 |
| 8 | Supply and installation of C-Curve MCB’s |  |  |  |
| a | 32 Amp 4 Pole MCB |  | Nos. | 6 |
| b | 20 Amp 4 Pole MCB |  | Nos. | 3 |
| 9 | Supply and installation of Heavy duty uPVC conduit, in wall chase, wall surface, slab etc, including all accessories, complete as required. Make: AKG |  |  |  |
|  | 40mm dia |  | meter | 30 |
| 10. | Socket Mounted Metal Box with Cover, 1 No. Plug (2 Pin + Earth), 1 No. 20A Single Pole MCB, Wiring Accessories as needed ( Brand : Legrand/ L&t) |  | Nos. | 3 |

Commercial Bid: (in separate sealed envelope)

Bid for Supply and Installation Work 1.5 TR Split 5 Star Inverter Supper Efficient Air Conditioner for Boys Hostels 1, 2 & 3 in Warden Office

| S No | PARTICULARS | UNIT | QTY | Rate | AMOUNT |
| --- | --- | --- | --- | --- | --- |
| A | Supply of Air conditioning system of following items |  |  |  |  |
|  | Supply of 1.5 TR 5 Star Split Air Conditioner with 1 year Standard Manufacturer Warranty and 5 Year compressor Warranty. White (Copper Condenser) 1.5 TR Split type air conditioning machine with 1 nos. indoor unit & 1 nos. 1.5 TR outdoor unit. Including all accessories. Preferred Makes: Hitachi / Daikin/Voltas/Carrier/EESL |  |  |  |  |
|  | Outdoor Unit 1.5TR |  |  |  |  |
|  | Outdoor condensing unit shall comprise of 1 nos. Rotary /reciprocating/ scroll compressor of 1.5 TR capacity. Air cooled condenser having copper tube with mechanically bonded aluminum fins of adequate heat transfer area as per manufacturer’s standard, complete with fan and fan motor of required capacity with independent circuit complete with interconnecting piping, wiring and controls. |  |  |  |  |
|  | Indoor Unit 1.5 TR |  |  |  |  |
|  | Indoor unit of 1.5 TR capacity, consisting of multi row cooling coil having copper tube with mechanically bonded aluminum fins, thermostat expansion valve, dynamically balanced centrifugal blower driven by TEFC squirrel cage induction motor, cleanable synthetic filter, insulated drain pan complete with microprocessor control for efficient operation, inter connecting copper tube duly insulated with nitrile rubber molded section and cordless hand set. |  |  |  |  |
|  | Machine with 1 outdoor and 1 indoor units | Nos. | 3 |  |  |
| B | Supply and Installation of Air conditioning system of following items |  |  |  |  |
| 1 | Lifting, shifting, positioning, installation, testing and commissioning of outdoor units, fittings (Imported Y-joints & header etc.) remote controls of indoor units, including gas charging with R32/R410A gas as required, complete as per specification. pressure testing of concealed indoor units |  |  |  |  |
| a | Indoor Unit _ 1.5 TR | Nos | 3 |  |  |
| b | Outdoor Unit_ 1.5 TR | Nos. | 3 |  |  |
| 2 | Refrigerant Copper Piping |  |  |  |  |
|  | Interconnecting refrigerant pipe work with (12.5mm/6.35 mm thick) closed cell elastomeric nitrile rubber tubular insulation between each set of indoor & outdoor units as per specifications, all piping inside the room shall be properly supported with MS hanger. | meter | 60 |  |  |
| 3 | Drain Piping |  |  |  |  |
|  | Providing and fixing rigid PVC piping complete with fittings, supports as per specifications and duly insulated with 6 mm thick closed cell nitrile rubber insulation. |  |  |  |  |
| a | 25 mm dia ( Brand : Supreme/Kisan/AKG) | Meter | 30 |  |  |
| 4. | Providing and fixing of MS Wall/ floor mounted stand for outdoor unit | Nos. | 3 |  |  |
| 5 | Power and control cabling between indoor and outdoor / ac panel, HAT, etc. Make:-Polycab/KEI/RR/APAR) |  |  |  |  |
| 1 | 3 Core 2.5 sq mm cu flexible cable | Meter | 100 |  |  |
| 6 | Supply and installation of 4 core 4 sq mm copper armored cables DB to Panel. (Make:-Polycab/KEI/RR/APAR) | Meter | 200 |  |  |
| 7 | Supply and installation of Single Door, MS Powder coated Single phase 8 way Distribution board, with all accessories. | Nos. | 3 |  |  |
| 8 | Supply and installation of C-Curve MCB’s |  |  |  |  |
| a | 32 Amp 4 Pole MCB | Nos. | 6 |  |  |
| b | 20 Amp 4 Pole MCB | Nos. | 3 |  |  |
| 9 | Supply and installation of Heavy duty uPVC conduit, in wall chase, wall surface, slab etc, including all accessories, complete as required. Make: AKG |  |  |  |  |
|  | 40mm dia | meter | 30 |  |  |
| 10. | Socket Mounted Metal Box with Cover, 1 No. Plug (2 Pin + Earth), 1 No. 20A Single Pole MCB, Wiring Accessories as needed ( Brand : Legrand/ L&t) | Nos. | 3 |  |  |
| Total |  |  |  |  |  |
| GST |  |  |  |  |  |
| Total including GST |  |  |  |  |  |

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should be including all (Packing, forwarding, Transit Insurance, Transportation Loading/unloading, Installation etc.). Loading/unloading up to 50 Mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- Bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

All charges applicable shall be clearly mentioned with the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

Signature with seal