The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

“The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, setup as a Non Profit Making institute located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposal from competent vendors for “Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand”. Bidders can submit their sealed offer/s at the following address by Speed-Post/ Registered Post/ By-hand (but not by Courier) before 05:00 PM on 10.02.2024.

Bids shall be addressed to the undersigned and deposited in the tender box available at main gate of Institute after marking due entries.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Email: directoroffice@lnmiit.ac.in

Bidders can also submit their offer/s via Email with password protected document/file at the below mentioned email IDs (E-mail must sent on both mail ID) before 05:00 PM on 10.02.2024.

The Password protected document/file to be sent to purchase officer at the email id: purchase.officer@lnmiit.ac.in and password should be sent to Chairman-PCC at the email id: chairman.pcc@lnmiit.ac.in .

purchase.officer@lnmiit.ac.in

chairman.pcc@lnmiit.ac.in

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory are required to be submitted in two separate envelopes/files. Both envelopes/files should be duly marked as “Technical bid for “Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand” and “Commercial Bid for “Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand”.  respectively. Both Envelopes shall be enclosed in a single envelope bearing the heading “Bid for Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand)”. Bids are liable to be rejected if any or both of the technical or commercial offers are found in open condition or required information is not found with the offer.

Bids can be sent via email as per the process mentioned above.

Technical Bid: (in a separate sealed envelope)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turn over for the last three years to be mentioned. (Copy to be enclosed)

- List of the client to whom the vendor has delivered the goods or provided the services in past.

- Specification as mentioned below, shall be provided as per the details given below:

Scope of work, Technical data sheet and Specification of the item/s

Scope of work: 	Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand

| 1 | MODULAR UPS SPECIFCATION |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| S.N | Description | Specification (Minimum) |  |  |  |  |  |
| 1. | General Specifications |  |  |  |  |  |  |
| i | Modular UPS Topology | Online Double Conversion VFI SS 111 |  |  |  |  |  |
| ii | Architecture of the UPS | Modular, scalable, redundant based Power Modules of 5KVA to 10KVA |  |  |  |  |  |
| iii | Power Cabinet Capacity | 30KVA |  |  |  |  |  |
| iv | Real & Active power in Each Power Module | Output Power Factor should be Unity (KVA=KW) |  |  |  |  |  |
| v | Redundancy in Control Panels/ Board | Multiple Control panel (Mandatory) |  |  |  |  |  |
| vi | Redundancy in Power Modules | All Power Modules should deliver power to load with no standby mode. |  |  |  |  |  |
| vii | Hot Plug- Hot Swap | In redundant configurations the UPS must be able to supply and protect the load, also during the replacement of faulty module and no bypass switch is needed |  |  |  |  |  |
| viii | In/Out phase Configuration | Three phases |  |  |  |  |  |
| ix | Neutral | Neutral Passing through |  |  |  |  |  |
| x | Redundancy in Battery Bank | Supplier had to provide two Parallel Bank for maintaining the redundancy in Battery Bank |  |  |  |  |  |
| xi | Bypass type | Static and electro mechanic (Maintenance Bypass) |  |  |  |  |  |
| xii | Transfer time | Zero as per IEC 62040-3 |  |  |  |  |  |
| 2. | Input |  |  |  |  |  |  |
| i | Nominal Voltage | 400 V three phase |  |  |  |  |  |
| ii | Voltage range | -15% +15% |  |  |  |  |  |
| iii | Frequency | 45-65 Hz |  |  |  |  |  |
| iv | THDIin | < 3% al 100% of nominal load |  |  |  |  |  |
| v | Power Factor | > 0.99 @ 50% load |  |  |  |  |  |
| 3. | Output with mains (AC-AC) |  |  |  |  |  |  |
| i | Nominal voltage | 400 V three phase |  |  |  |  |  |
| ii | UPS should have other Input & Output Phase Onsite configuration facility also | 1Phase (I/P) /1Phase (O/P) or 3Phase (I/P) /1Phase (O/P) |  |  |  |  |  |
| iii | Nominal power | 30KVA |  |  |  |  |  |
| iv | Active power | 30KW |  |  |  |  |  |
| v | Voltage variation (static) | ± 1% |  |  |  |  |  |
| vi | Voltage variation (dynamic 0-100%; 100-0%) | ± 1% |  |  |  |  |  |
| vii | THDv on nominal power | < 1 % |  |  |  |  |  |
| viii | Frequency | 50 Hz +/- 0.1% |  |  |  |  |  |
| ix | Frequency tolerance | Synchronized with input frequency or ± 1% free run |  |  |  |  |  |
| x | Current Crest Factor | 2.5:1 accordingly with IEC EN62040-3 |  |  |  |  |  |
| xi | Overall Double Conversion Efficiency | Upto 96% |  |  |  |  |  |
| xii | Eco mode | > 98% |  |  |  |  |  |
| xiii | Overload capability: | Minimum 115% load rate with no bypass intervention for 5 min; Minimum 135% load rate with no bypass intervention for 30 seconds |  |  |  |  |  |
| 4. | UPS Power Module |  |  |  |  |  |  |
| i | Each Power Module will be composed by following functional blocs | Inverter, Booster, Battery Charger, Rectifier/PFC, Automatic Bypass |  |  |  |  |  |
| 5. | Battery |  |  |  |  |  |  |
| i | Type | Lead Acid, sealed, free maintenance VRLA |  |  |  |  |  |
| ii | Nominal UPS Battery Voltage | 240 Volt DC |  |  |  |  |  |
| iii | Backup Time Required is of 2 Hrs | Minimum 48000 VAH for 120 min backup on 15KVA load (Vendor should develop redundancy in Battery Bank also i.e 60mins + 60 mins) |  |  |  |  |  |
| iv | Battery charger type | Each power module should have individual battery charger |  |  |  |  |  |
| v | Charging Cycle | Intelligent with boost charge and advanced management |  |  |  |  |  |
| vi | Battery Management | Battery test either automatically or upon the user’s request |  |  |  |  |  |
| vii | Battery Cabinet | MS Rack with Circuit Breaker |  |  |  |  |  |
| 6. | Environmental specs |  |  |  |  |  |  |
| i | Noise level @ 1m | 50 - 65 dBA |  |  |  |  |  |
| ii | Working temperature range | from 0°C to +40°C |  |  |  |  |  |
| iii | Humidity range | 20-95% not condensing |  |  |  |  |  |
| iv | Protection degree | IP21 |  |  |  |  |  |
| 7. | Others |  |  |  |  |  |  |
| i | Remote Monitoring | Through SNMP Card (To be provided) |  |  |  |  |  |
| ii | UPS OEM Certificates | Should have ISO 9001, 14001 & 45001 |  |  |  |  |  |
| iii | Product Enviornmental Profile | UPS Model should be PeP Certified (Must) |  |  |  |  |  |
| iv | Product Standards | EN 62040-1, EN 62040-2, EN 62040-3 |  |  |  |  |  |
| v | Product Marking | UPS should be UE /CE approved |  |  |  |  |  |
| vi | SMF Batteries Brand | Exide/ Quanta (Amaron) |  |  |  |  |  |
| vii | UPS Brand | Numeric (Legrand), ABB, Socomec |  |  |  |  |  |
| 8. | Warranty on UPS & Batteries |  |  |  |  |  |  |
| i | Warranty on UPS & Batteries | Onsite 24 months on UPS & 2 years on SMF Batteries from date of Installation or 24 months on UPS & SMF Batteries from date of delivery, whichever happens earlier |  |  |  |  |  |

| S.No. | Particulars | Make | Qty. with UOM |
| --- | --- | --- | --- |
| 1. | Supply, Installation, Testing & Commissioning of 30 KVA Three Phase Online Modular UPS System with Two years warranty | Numeric/APC /Socomec/ABB | 1 Nos |
| 2. | 12V/100 AH SMF UPS Battery with 120 min. Backup | Exide/Amaron | 40 Nos. |
| 3. | Battery MS Fabricated Stand with Copper Interlink cables |  | 1 nos. |

Commercial Bid: (in separate sealed envelope)

Bid for Supply, installation, testing and commissioning of 30 KVA Three Phase online Modular UPS System with Batteries and MS Fabricated Stand

| S. No. | Particulars | Make | Qty. | UOM | Rate | Amount |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Supply, Installation, Testing & Commissioning of 30 KVA Three Phase Online Modular UPS System with Two years warranty | Numeric/APC /Socomec/ABB | 1 | Nos. |  |  |
| 2 | 12V/100 AH SMF UPS Battery with 120 min. Backup | Exide/Amaron | 40 | Nos. |  |  |
| 3 | Battery MS Fabricated Stand with Copper Interlink cables |  | 1 | Nos. |  |  |
| 4 | Transportation charges |  | 1 | Nos. |  |  |
|  | Total |  |  |  |  |  |
|  | GST_______ |  |  |  |  |  |
| TOTAL (including taxes) |  |  |  |  |  |  |

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should include all (Packing, forwarding, Transit Insurance, Transportation Loading/unloading, Installation etc.). Loading/unloading up to 50 Mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- Bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

All charges applicable shall be clearly mentioned with the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final and nothing extra shall be paid extra.

Signature with seal