The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposal from competent vendors for “Supply, installation, Testing and commission work of Pole Lighting on Boundary wall”. Bidders can submit their sealed offer/s at the following address by Speed-Post/ Registered Post/ By-hand (but not by Courier)/ before 05:00 PM on 09.03.2024.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the Institute after marking due entries.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Email: directoroffice@lnmiit.ac.in

Bidders can also submit their offer/s via Email with password protected document/file at the below mentioned email IDs (E-mail must sent on both mail ID) before 05:00 PM on 09.03.2024.

The Password protected document/file to be sent to purchase officer at the email id: purchase.officer@lnmiit.ac.in and password should be sent to Chairman-PCC at the email id: chairman.pcc@lnmiit.ac.in .

purchase.officer@lnmiit.ac.in

chairman.pcc@lnmiit.ac.in

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory are required to be submitted in two separate envelopes/files. Both envelopes/files should be duly marked as “Technical bid for “Supply, installation, Testing and commission work of Pole Lighting on Boundary wall” and “Commercial Bid for “Supply, installation, Testing and commission work of Pole Lighting on Boundary wall” respectively. Both Envelopes shall be enclosed in a single envelope bearing the heading “Bid for Supply, installation, Testing and commission work of Pole Lighting on Boundary wall”. Bids are liable to be rejected if any or both of the technical or commercial offers are found in open condition or required information is not found with the offer.

Bids can be sent via email as per the process mentioned above.

Technical Bid: (in a separate sealed envelope)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turn over for the last three years to be mentioned. (Copy to be enclosed)

- List of the client to whom the vendor has delivered the goods or provided the services in past.

- Specification as mentioned below, shall be provided as per the details given below:

Scope of work, Technical data sheet and Specification of the item/s

Scope of work: 	Supply, installation, Testing and commission work of Pole Lighting on Boundary wall for 150 PEB Office to Kabaddi Playground along with the Boundary wall

| The LNM Institute of Information Technology |  |  |  |
| --- | --- | --- | --- |
| Name of the work : Incubation Center to kabaddi playground of Institute Lighting on boundary Wall |  |  |  |
| S. No. | DESCRIPTION OF ITEM (S) | UNIT | QTY |
| 1 | Pole of MS Pipe | Nos. | 18 |
|  | Supplying, fixing, testing and commissioning of following sizes (NB) of ISI marked M.S pipe. including painting of pipes and fittings with silver waterproof paint over a coat of ready mixed primer and complete in all respect as required. (Make : TATA/JINDAL/SURY/Apollo ) |  |  |
| a. | Length of pole: 3 meters |  |  |
| b. | Dia of Pole: 50 mm |  |  |
| c. | Thickness of pole : 2.5 mm to 3 mm |  |  |
| d. | MS Pole Base Plate with Hole Size : 300mm x 300mm x 10mm | Nos. | 18 |
| e. | MS J Hook bolt with Nut (MS J bolt of Dia: 12mm, MS J bolt of Length : 1200mm, Nut : 50 Nos.) | Nos. | 72 |
| f. | Surface Coat of red oxide primer |  |  |
| g. | Surface Coat of metallic silver |  |  |
| 2 | MS Pole Arm with Cap |  |  |
|  | Supplying, fixing, testing and commissioning of following sizes (NB) of ISI marked M.S Arm. including painting of MS Arm and fittings with silver waterproof paint over a coat of ready mixed primer and complete in all respect as required. (Make: TATA/JINDAL/SURY/Aapollo ) |  |  |
| a. | MS Single Arm With Cap (Size: Cap_ 300mm, Arm _ 450mm +100mm ) | Nos. | 2 |
| b. | MS double Arm With Cap ( Size : Cap_ 300mm, Arm : (450mm +100mm )x 2) | Nos. | 16 |
| 3 | Excavation Work for Pole Foundation |  |  |
|  | Excavation work for pole foundation in including dressing of sides, ramming of bottoms stacking the excavated earth at site and filling with the excavated soil all excavated areas. |  |  |
| a) | Foundation Dimensions(L x W x D): 600mm x 600mm x 750mm | Nos. | 18 |
| 4 | Pole Foundation of Civil Work |  |  |
|  | Providing, laying & testing cast - in - place structural controlled cement concrete grade M25 using 20mm down coarse aggregates but including cost of centering & cement, shuttering and steel reinforcement |  |  |
| a | Filling RCC Grade in pole Foundation Dimensions (L x W x D): 600mm x 600mm x 1250mm | Nos | 18 |
| b. | 12-15 mm thick water proof plaster to masonry & concrete surfaces in cement mortar 1:4 ( 1 cement : 4 fine & coarse sand in equal proportion) applied with a floating coat of neat cement , finished smooth and curved including corner / edge beads of approved material etc and including cost of cement. pole Foundation Dimensions (L x W x D): 600mm x 600mm x 1250mm | Nos | 18 |
| 5 | 3 Phase Electrical Waterproof Junction Boxes For Street Light Poles | Nos. | 18 |
|  | Supplying, fixing, testing and commissioning of following sizes (NB) of ISI marked 3phase electrical bus bar box with complete accessories. |  |  |
| a. | Rated Voltage :415 V |  |  |
| b. | Size of Box (L x W X H ): 300mm x 200mm x 150mm |  |  |
| c. | Rated Current : 100 Amper |  |  |
| d. | Mounting : Wall Mounting |  |  |
| e. | Ingress protection : IP66 |  |  |
| f. | MCB : 6A |  |  |
| g. | 2.0/1.6mm CRCA Sheet steel enclosure duly Powder coated with RAL - 7035 Including M.S.wall Maunted : TATA/SAIL |  |  |
| h. | Danger Warning Electrical Panel Waterproof Sticker : Size : 150 x 100 mm, Colour : Red & White , Shape : Rectangle |  |  |
| i. | Conical - Insulators And Busbar Supports : 8mm |  |  |
| 6 | CABLES |  |  |
| 1 | Supplying of following sizes of XLPE insulated armored copper conductor power cable of 1.1 KV grade. Make : Polycab/ KEI |  |  |
| a | 4 core x 4 Sqmm Armored Copper Cable | Meter | 400 |
| b. | 3 core x 1.5 Sqmm Flexible Copper Cable | Meter | 200 |
| 2 | Laying and fixing of XLPE insulated Aluminum/copper Conductor Armored/flexible Cables of 1.1 KV grade of following size on ground/ cable tray / surface mounted/pole inner/ stone wall boundary with MS saddles along with misc. accessories like Cable Ties / Saddles / Cable Tags etc. |  |  |
| a | 4 core x 4 Sqmm Armored Copper Cable (Stone Boundary Wall ) | Meter | 400 |
| b. | 3 core x 1.5 Sqmm Flexible Copper Cable ( Pole inner side ) | Meter | 200 |
| 3 | Digging and back filling 450mm / 600 mm wide and 750 mm deep trench for laying cable for LT cables as required along with sand and brick lining as per IS specification. | meter | 80 |
| 4 | Supplying and making end termination with double compression, brass compression gland including providing and crimping with aluminum solder less lugs/ ferrules for XLPE insulated armored power aluminum conductor cable of 1.1 KV grade as required. |  |  |
| a | 4 core x 4 Sqmm Armored Copper Cable (Stone Boundary Wall) | Nos. | 36 |
| b. | 3 core x 1.5 Sqmm Flexible Copper Cable (Pole inner side ) | Nos. | 36 |

Commercial Bid: (in separate sealed envelope)

Supply, installation, Testing and commission work of Pole Lighting on Boundary wall for 150 PEB Office to Kabaddi Playground along with the Boundary wall

| The LNM Institute of Information Technology |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Name of the work : Incubation Center to kabaddi playground of Institute Lighting on boundary Wall |  |  |  |  |  |
| S. No. | DESCRIPTION OF ITEM (S) | UOM | QTY | Rate | Amount |
| 1 | Pole of MS Pipe | Nos. | 18 |  |  |
|  | Supplying, fixing, testing, and commissioning of following sizes (NB) of ISI marked M.S pipe. including painting of pipes and fittings with silver waterproof paint over a coat of ready mixed primer and complete in all respect as required. (Make: TATA/JINDAL/SURY/Apollo ) |  |  |  |  |
| a. | Length of pole: 3 meters |  |  |  |  |
| b. | Dia of Pole: 50 mm |  |  |  |  |
| c. | Thickness of pole: 2.5 mm to 3 mm |  |  |  |  |
| d. | MS Pole Base Plate with Hole Size : 300mm x 300mm x 10mm | Nos. | 18 |  |  |
| e. | MS J Hook bolt with Nut (MS J bolt of Dia: 12mm, MS J bolt of Length: 1200mm, Nut : 50 Nos.) | Nos. | 72 |  |  |
| f. | Surface Coat of red oxide primer |  |  |  |  |
| g. | Surface Coat of metallic silver |  |  |  |  |
| 2 | MS Pole Arm with Cap |  |  |  |  |
|  | Supplying, fixing, testing and commissioning of following sizes (NB) of ISI marked M.S Arm. including painting of MS Arm and fittings with silver waterproof paint over a coat of ready mixed primer and complete in all respect as required. (Make: TATA/JINDAL/SURY/Aapollo ) |  |  |  |  |
| a. | MS Single Arm With Cap (Size: Cap_ 300mm, Arm _ 450mm +100mm ) | Nos. | 2 |  |  |
| b. | MS double Arm With Cap ( Size : Cap_ 300mm, Arm : (450mm +100mm )x 2) | Nos. | 16 |  |  |
| 3 | Excavation Work for Pole Foundation |  |  |  |  |
|  | Excavation work for pole foundation in including dressing of sides, ramming of bottoms stacking the excavated earth at site and filling with the excavated soil all excavated areas. |  |  |  |  |
| a) | Foundation Dimensions(L x W x D): 600mm x 600mm x 750mm | Nos. | 18 |  |  |
| 4 | Pole Foundation of Civil Work |  |  |  |  |
|  | Providing, laying & testing cast - in - place structural controlled cement concrete grade M25 using 20mm down coarse aggregates but including cost of centering & cement, shuttering and steel reinforcement |  |  |  |  |
| a | Filling RCC Grade in pole Foundation Dimensions (L x W x D): 600mm x 600mm x 1250mm | Nos | 18 |  |  |
| b. | 12-15 mm thick water proof plaster to masonry & concrete surfaces in cement mortar 1:4 ( 1 cement : 4 fine & coarse sand in equal proportion) applied with a floating coat of neat cement , finished smooth and curved including corner / edge beads of approved material etc and including cost of cement. pole Foundation Dimensions (L x W x D): 600mm x 600mm x 1250mm | Nos | 18 |  |  |
| 5 | 3 Phase Electrical Waterproof Junction Boxes For Street Light Poles | Nos. | 18 |  |  |
|  | Supplying, fixing, testing and commissioning of following sizes (NB) of ISI marked 3phase electrical bus bar box with complete accessories. |  |  |  |  |
| a. | Rated Voltage :415 V |  |  |  |  |
| b. | Size of Box (L x W X H ): 300mm x 200mm x 150mm |  |  |  |  |
| c. | Rated Current : 100 Amper |  |  |  |  |
| d. | Mounting : Wall Mounting |  |  |  |  |
| e. | Ingress protection : IP66 |  |  |  |  |
| f. | MCB : 6A |  |  |  |  |
| g. | 2.0/1.6mm CRCA Sheet steel enclosure duly Powder coated with RAL - 7035 Including M.S.wall Maunted : TATA/SAIL |  |  |  |  |
| h. | Danger Warning Electrical Panel Waterproof Sticker : Size : 150 x 100 mm, Colour : Red & White , Shape : Rectangle |  |  |  |  |
| i. | Conical - Insulators and Busbar Supports: 8mm |  |  |  |  |
| 6 | CABLES |  |  |  |  |
| 1 | Supplying of following sizes of XLPE insulated armored copper conductor power cable of 1.1 KV grade. Make: Polycab/ KEI |  |  |  |  |
| a | 4 core x 4 Sqmm Armored Copper Cable | Meter | 400 |  |  |
| b. | 3 core x 1.5 Sqmm Flexible Copper Cable | Meter | 200 |  |  |
| 2 | Laying and fixing of XLPE insulated Aluminum/copper Conductor Armored/flexible Cables of 1.1 KV grade of following size on ground/ cable tray / surface mounted/pole inner/ stone wall boundary with MS saddles along with misc. accessories like Cable Ties / Saddles / Cable Tags etc. |  |  |  |  |
| a | 4 core x 4 Sqmm Armored Copper Cable (Stone Boundary Wall ) | Meter | 400 |  |  |
| b. | 3 core x 1.5 Sqmm Flexible Copper Cable ( Pole inner side ) | Meter | 200 |  |  |
| 3 | Digging and back filling 450mm / 600 mm wide and 750 mm deep trench for laying cable for LT cables as required along with sand and brick lining as per IS specification. | meter | 80 |  |  |
| 4 | Supplying and making end termination with double compression, brass compression gland including providing and crimping with aluminum solder less lugs/ ferrules for XLPE insulated armored power aluminum conductor cable of 1.1 KV grade as required. |  |  |  |  |
| a | 4 core x 4 Sqmm Armored Copper Cable (Stone Boundary Wall) | Nos. | 36 |  |  |
| b. | 3 core x 1.5 Sqmm Flexible Copper Cable (Pole inner side ) | Nos. | 36 |  |  |

| Total |  |
| --- | --- |
| GST |  |
| Total including GST |  |

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should be including all (Packing, forwarding, Transit Insurance, Transportation Loading/unloading, Installation etc.). Loading/unloading up to 50 Mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- Bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

- If any vendor is apply for first time in the LNMIIT, Jaipur then they must submit their last three years working/ supplying record in the particular work domain.

- Vendor should have to submit their bids in the LNMIIT format other than that given format shall be rejected.

All charges applicable shall be clearly mentioned with the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

Signature with seal