The LNM Institute of Information Technology, Jaipur

TENDER NOTICE

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “Supply and Installation of  1 TR Split Type 5 Star Air Conditioner in Microwave Lab”. Bidders can submit their sealed offer/s at the following address by Email/Speed-Post/ Registered Post/ By-hand (but not by Courier)/ before 05:00 PM on 20.03.2024.

Bids shall be addressed to the undersigned and deposited in the tender box available at the main gate of the Institute after marking due entries.

Director

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

Email: directoroffice@lnmiit.ac.in

Bidders can also submit their offer/s via Email with password protected document/file at the below mentioned email IDs (E-mail must sent on both mail ID) before 05:00 PM on 20.03.2024.

The Password protected document/file to be sent to purchase officer at the email id: purchase.officer@lnmiit.ac.in, quote@lnmiit.ac.in and password should be sent to Chairman-PCC at the email id: chairman.pcc@lnmiit.ac.in .

purchase.officer@lnmiit.ac.in

quote@lnmiit.ac.in

chairman.pcc@lnmiit.ac.in

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory are required to be submitted in two separate envelopes/files. Both envelopes/files should be duly marked as “Technical bid for “Supply and Installation of 1 TR Split Type 5 Star Air Conditioner in Microwave Lab” and “Commercial Bid for “Supply and Installation of 1 TR Split Type 5 Star Air Conditioner in Microwave Lab” respectively. Both Envelopes shall be enclosed in a single envelope bearing the heading “Bid for “Supply and Installation of 1 TR Split Type 5 Star Air Conditioner in Microwave Lab”. Bids are liable to be rejected if any or both technical or commercial offers are found in open condition or required information is not found with the offer.

Bids can be sent via email as per the process mentioned above.

Technical Bid: (in a separate sealed envelope)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turnover for the last three years to be mentioned. (Copy to be enclosed)

- List of the clients to whom the vendor has delivered the goods or provided the services in the past.

- Specification as mentioned below, shall be provided as per the details given below:

Technical data sheet and Specification of the item/s

Technical Specifications

Supply and Installation of 1 TR Split Type 5 Star Air Conditioner in Microwave Lab

| 1 Ton 5 Star inverter type split AC |  |  |
| --- | --- | --- |
| S. No. | Technical Specifications |  |
| 1 | Capacity | 1 Ton |
| 2 | Rating | 5 Star |
| 3 | Inverter Technology | Yes |
| 4 | Brand | Voltas/Blue Star/Daikin |
| 5 | Air Conditioner Type | Split |
| 6 | Refrigerant Type | R32 |
| 7 | Condenser Coil Type | Copper |
| 8 | Indian Sessional Energy Efficiency Ratio | 5.2 |
| 9 | Power Consumption | 1150 Watt |
| 10 | Voltage Range (Stabilizer Inside) | 130-285V |
| 11 | Motor Warranty | 1 Year warranty on condenser & 10-year warranty on compressor |

| S No | PARTICULARS | UNIT | Make |
| --- | --- | --- | --- |
| 1. | Supply and installation of 1 Nos. of Indoor and Outdoor Units | Nos. |  |
| 2. | Interconnecting refrigerant pipe work with closed cell elastomeric nitrile rubber tubular insulation as per specified manual. | Mtr. |  |
| 3. | Providing and fixing rigid PVC piping complete with fittings and supports as per specifications. (Brand: Supreme/Kisan/AKG) | Mtr. |  |
| 4. | Providing and fixing of Floor Mounted stand for the outdoor unit (heavy Duty) (Brand: Supreme/Kisan/AKG) | Nos. |  |
| 5. | Power and control cabling between indoor and outdoor, FRLS copper wire Make: -Polycab/KEI/ Havells) 3.5 C x 2.5 Sqmm | Mtr. |  |

Commercial Bid: (in a separate sealed envelope)

Supply and Installation of 1 TR Split Type 5 Star Air Conditioner in Microwave Lab

| S No | PARTICULARS | UNIT | QTY | Rate | AMOUNT |
| --- | --- | --- | --- | --- | --- |
| 1 | Supply and installation of 1 Nos. of Indoor and Outdoor Units as per technical specifications provided. | Nos. | 1 |  |  |
| 2 | Interconnecting refrigerant pipe work with closed cell elastomeric nitrile rubber tubular insulation as per specified manual. | Mtr. | 7 |  |  |
| 3 | Providing and fixing rigid PVC piping complete with fittings and supports as per specifications. (Brand: Supreme/Kisan/AKG) | Mtr. | 5 |  |  |
| 4 | Providing and fixing of Floor Mounted stand for the outdoor unit (heavy Duty) (Brand: Supreme/Kisan/AKG) | Nos. | 1 |  |  |
| 5 | Power and control cabling between indoor and outdoor, FRLS copper wire Make: -Polycab/KEI/ RR) 3.5 C x 2.5 Sqmm | Mtr. | 8 |  |  |
| 6. | Cartage | Nos | 1 |  |  |
|  | Total |  |  |  |  |
|  | GST |  |  |  |  |
|  | Total with GST |  |  |  |  |

- Vendor should use the same format & and mention the item make otherwise vendor bid can be rejected.

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned, especially by him.

- The prices should include all (Packing, forwarding, Transit Insurance, Transportation Loading/unloading, Installation, etc.). Loading/unloading up to 50 Mtr. shall be done by the supplier.

- Before submitting a bid, vendors should visit the site & and verify details as payment will be made on actual work performed.

- The bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- The bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- The bid should be on the company’s letterhead and should be submitted in the LNMIIT format only.

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Payment will be made on the actual quantity commissioned/installed.

- The vendor should submit the bid in the same format otherwise the bid can be rejected.

- The vendor should provide a photocopy of the cheque/canceled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meetings and pre-bid site visits can be done before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and the solicitation of documents.

All charges applicable shall be clearly mentioned in the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid.

Signature with seal