TENDER DOCUMENT

for

Supply, Installation, Testing, and Commissioning of External Fire Fighting, Fire Alarm and fire Extinguisher Work

From

The LNM institute of Information Technology

Rupa Ki Nangal, Post - Sumel, Via – Jamdoli,

Jaipur – 302 031 (Raj.) INDIA

The LNM Institute of Information Technology, Jaipur

TENDER DOCUMENT

The LNM Institute of Information Technology, Jaipur is a Deemed-to-be-University, set up as a Non-Profit Making institute engaged in imparting higher learning in Engineering, Technology and Science. We are located at Gram-Rupa Ki Nangal, Post-Sumel, Via-Jamdoli, Jaipur, Pin 302031 Rajasthan, under the joint venture of the Government of Rajasthan and Lakshmi & Usha Mittal Foundation.

The institute invites proposals from competent vendors for “Supply, Installation, Testing, and Commissioning of External Fire Fighting, Fire Alarm and fire Extinguisher Work”. Bidders can submit their sealed offers/s at the following address by Email/Speed-Post/ Registered Post/ By-hand (but not by Courier)/ before 05:00 PM on 31-03-2024.

Finance Officer

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

www.lnmiit.ac.in

Bidders can also submit their offer/s via Email with password protected document/file at the below mentioned email IDs before 05:00 PM on 31-03-2023.

The Password protected document/file along with password to be sent at the email id: Chairman-PCC subcommittee chairman.pcc.projects@lnmiit.ac.in

Bid Process:

Technical & Commercial details on the company’s letterhead, duly signed and sealed by the authorized signatory are required to be submitted in two separate envelopes/files. Both envelopes/files should be duly marked as “Technical bid for “Supply, Installation, Testing, and Commissioning of External Fire Fighting, Fire Alarm and fire Extinguisher Work” and “Commercial Bid for “Supply, Installation, Testing, and Commissioning of External Fire Fighting, Fire Alarm and fire Extinguisher Work” respectively. Both Envelopes shall be enclosed in a single envelope bearing the heading “Bid for “Supply, Installation, Testing, and Commissioning of External Fire Fighting, Fire Alarm and fire Extinguisher Work”.

Bids are liable to be rejected if any or both technical or commercial offers are found in open condition or required information is not found with the offer.

Technical Bid: (in a separate sealed envelope)

While submitting quotations, the following procedure/ formalities and conditions may kindly be adhered.

- Company profile or brief note about the bidder's company, PAN number, and GST number should be submitted by the Vendor.

- The List of Directors/Partners/Proprietor/Members of the Firm to be attached.

- Detail of other associated/sister concerns (if any) of Directors/Partners/ Proprietor/ Members to be provided.

- Turnover for the last three years to be mentioned. (Copy to be enclosed)

- List of the client to whom the vendor has delivered the goods or provided the services in the past.

- Details of similar works carried out during FY 2020-21, 2021-22, 2022-23. (Attach copies)

| Year | Name of the Organization | Work order ref. and Date |
| --- | --- | --- |

- Specification as mentioned below, shall be provided as per the details given below:

Name and signature of Vendor

Seal

Date:

Place:

Technical Specification

TECHNICAL SPECIFICATIONS FOR FIREFIGHTING

- APPLICABLE CODES AND STANDARDS:

All equipment, supply, erection, testing and commissioning shall comply with the requirements of Indian Standards and code of practice given below as amended upto the date of submission of Tender. All equipment and material being supplied shall meet the requirements of BIS and other relevant standard and codes.

MS Tube upto 150mm		-	IS:1239

MS Tubes above 150mm	-	IS:3589

Malleable Iron Fittings		-	IS:1239 -1982 (Part-I&II) Cast Iron Sluice Valves					-	IS: 780 - 1984

Check Valves			-	IS:5312 - 1975

Internal/External Fire Hydrant Valve	IS:5290 -1983

Rubberized Fabric Lined Hose		-	IS: 636

Couplings, Branch Pipe, Nozzles	-	IS: 903

First Aid Fire Hose (Rubber)		-	IS:5132-1969

First Air Hose Reel			-	IS: 884 – 1969

- Pipe Fittings

Pipe fittings mean tees, elbows, couplings, unions, flanges, reducers etc and all such connecting devices that are needed to complete the piping work in its totality.

Forged steel screwed type/ Welded  fitting shall be used for pipes of 50 mm dia & below.

Fabricated fittings used on pipe size 65mm & above shall be fabricated, welded in workshops.

- PAINTING

All Hydrant and Sprinkler pipes shall be painted with post officered colour paint. All M S pipes shall first be cleaned thoroughly before application of primer coat. After application of primer coat two coats of enamel paint shall be applied. Each coat shall be given minimum 24 hours drying time. No thinners shall be used. Wherever required all pipe headers shall be worded indicating the direction of the pipe and its purpose such as"TORISERNO.1"etc.Painting shall be expertly applied, the paint shall not over run on surfaces not requiring painting such as walls, surfaces etc. Nuts and bolts shall be painted black, while valves shall be painted blue.

- EXCAVATION

Excavation for pipe lines shall be in open trenches to levels and grades shown on the drawings or as required at site. Pipe lines shall be buried with a minimum cover of 1 meter or as shown on drawings. Wherever required Contractor shall support all trenches or adjoining structures with adequate timber supports, shoring and strutting.

On completion of testing in the presence of the Project Manager and pipe protection, trenches shall be back filled in150 mm layers and consolidated.

Contractor shall dispose off all surplus earth as directed by the Project Manager.

- ANCHOR /THRUSTBLOCK

Contractor shall provide suitably designed anchor blocks in cement concrete/steel support to cater to the excess thrust due to work hammer and high pressure Thrust blocks shall be provided at all bends, tees and such other location as determined by the Project Manager.

Exact  location, design, size and mix of the concrete blocks/steel support shall be as  shown  on  the  drawings  or as  directed  by  the  Project  Manager  prior  to execution of work.

- FIRE HYDRANTS External Hydrants

Contractor shall provide external hydrants. The hydrants shall be controlled by a cast iron wheel. Hydrants shall have instantaneous type 63mm dia outlets. The hydrants shall be single outlet conforming to IS: 5290 with bend and riser or required height to bring the hydrant to correct level above ground.

Contract or shall provide for each external fire hydrant two numbers of 63 mm dia. 15m long controlled percolation hose pipe with SS male and female instantaneous type couplings machine wound with copper wire (hose to IS:636 type certification), SS  branch  pipe with nozzle  to  IS:903.  This shall be measured and paid for separately.

Each hose cabinet shall be conspicuously painted with the letters “FIRE HOSE”.

Internal Hydrants

Contractor shall provide on each landing and other locations as shown on the drawings double headed SS landing valve with 100 mm dia inlet as per IS:5290, with shut off valves having cast iron wheels as shown on the drawings. Landing valve shall have flanged inlet and instantaneous type outlets as shown on the drawings.

Instantaneous outlets for fire hydrants shall best and   pattern and suitable for firehoses.

Contractor shall provide for each internal fire hydrant station two numbers of

63 mm dia. 15 m long rubberized fabric lined hose pipes with SS male and female instantaneous type coupling machine would with copper wire (hose to IS:636 type A and couplings to IS:903 with IS certification), fire hose reel, SS branch pipe with nozzle to IS:903. This shall be measured and paid for separately.

Contractor shall provide standard fire   hose reel s of 20 mm dia high pressure rubber hose 36m long with gunmetal nozzle, all mounted on a circular hose reel of heavy duty mild steel construction having cast-iron brackets. Hose reel shall be connected directly to the wet riser with an isolating valve. Hose reel shall conform toIS:884 and shall be mounted vertically.

Each internal hydrant hose cabinet shall be provided with a drain in the bottom plate. The drain point shall be lead away to then earnest general drain.

Each internal hydrant hose cabinet containing items as above shall also be provided with a nozzle spanner and a Fireman’s Axe. The cabinet shall be recessed in the wall as directed. This shall be measured and paid for separately.

Each hose cabinet shall be conspicuously painted with the letters “FIRE HOSE”.

- Fire Hose

All hose pipes shall be of 63 mm diameter RRL as required, conforming to IS:636. The hose shall be provided with SS delivery coupling. The hose shall be capable of withstanding a bursting pressure of 35.7 Kg/Sq.cm without undue leakage or sweating. Hose shall be provided with instantaneous spring-lock, type couplings.

19.	Branch Pipe, Nozzle

Branch pipes shall be of SS with loaded tin bronze ring at the discharge and to receive the nozzle and provided at the other with a leaded tin bronze ring to fit into the instantaneous coupling. Nozzle shall be of spray type of diameter of not less than 16mm and not more than 25mm.Nozzle shall be of loaded tin bronze branch pipe and nozzle shall be of instantaneous pattern conforming to Indian Standard -

20.	Hose Cabinet

Hose cabinet shall be provided for all internal and external fire hydrants. External Hose cabinets shall be fabricated from14 gauge MS powder coated sheet of fully welded construction with hinged double front door partially glazed (3 mm glass panel) with locking arrangement, stove enamelled fire red paint (shade No. 536 of IS:5) with “FIRE HOSE” written on it prominently (The word `FIRE HOSE’ shall be in letters of at least 35mm in height. The words shall be painted white on red back ground). Cabinet surfaces in contact with the walls shall not be powder coated but instead given two coats of anti-corrosive bit mastic paint.

Internal Hose Cabinet

Hose cabinet shall be of glass fronted with hinged door & lock. The cabinet shall be made of Aluminium hollow box section, powder coated to shade No.536 of IS:5.The hose cabinet shall be of size to accommodate the following and size is as per BOQ:

i.	Landing Valves (Single headed)

ii. Hose pipe

iii. Hose reel (30 mtr.)

iv. Branch pipes, nozzles (1 sets)

v. Fire man's axe and hand appliances

External Hose Cabinet

The hose cabinet shall be of size to accommodate the following:

- Single/Double headed yard hydrant valve

ii Hose pipe (2length of15m)

iii Branch pipes, nozzles (1 sets)

iv. Fireman's axe

Approved make of Materials.

| LIST OF APPROVED MAKES FOR FIRE FIGHTING SYSTEM |  |  |  |  |
| --- | --- | --- | --- | --- |
| SL. NO. |  | MATERIAL DESCRIPTION |  | NAME OF MANUFACTURER |
| 1 |  | G.I./ M.S Forged Steel fittings IS:1239 (Part-II) |  | VS / DRP / True Forge / Simless |
| 2 |  | MS Pipe |  | Jindal- Hissar/Appolo API/TATA |
| 3 |  | Gunmetal Valve (Fullway valve) |  |  |
| 4 |  | (a) Class–I |  | Zoloto / Castle/Atam / Leader/ Kartar / Kalpana |
| 5 |  | (b) Class-II |  | Zoloto / Castle/Atam / Leader/ Kartar / Kalpana |
| 6 |  | Ball valve |  | Zoloto / Castle/Atam / Leader/ Kartar / Kalpana |
| 7 |  | Butterfly Valve |  | Zoloto / Castle/Atam / Leader/ Kartar / Kalpana |
| 8 |  | Air Release Valve |  | Zoloto / Castle/Atam / Leader/ Kartar / Kalpana |
| 9 |  | Float valve (gunmetal) upto 40mm |  | Zoloto / Castle/Atam / Equivalent |
| 10 |  | Float valve (C.I) 50mm and above |  | Zoloto / Castle/Atam / Equivalent |
| 11 |  | Fire Extinguishers |  | Kalpex/Exflame/Swastik / Life Guard |
| 12 |  | Fire fighting first-aid hose reel |  | Kalpex/Exflame/Swastik / SB |
| 13 |  | Hose Reel |  | Kalpex/Exflame/Swastik /SB |
| 14 |  | Rubber Tubing |  | Kalpex/Exflame/Swastik /SB |
| 15 |  | Thermo Plastic Hose Reels |  | Kalpex/Exflame/Swastik / SB |
| 16 |  | R.R.L. Hose |  | Kalpex/Exflame/Swastik / SB |
| 17 |  | Fire Fighting Equipment not covered else where |  | Kalpex/Exflame/Swastik /SB |
| 18 |  | Landing Valves |  | Kalpex/Exflame/Swastik /SB |
| 19 |  | Welding rods |  | Manglam / Adani |
| LIST OF APPROVED MAKES FOR FIRE FIGHTING SYSTEM |  |  |  |  |  |
| SL. NO. | MATERIAL DESCRIPTION |  | NAME OF MANUFACTURER |  |  |
| 20 | Sprinklers/Escutcheon plate/Flexible Pipes |  | Kalpex/Exflame/Swastik |  |  |
| 21 | Deluge Valve/Water Curtain nozzles |  | Kalpex/Exflame/Swastik |  |  |
| 22 | Cables/Wires |  | Havells/Polycab/Finolex |  |  |
| 23 | Cable Glands |  | Dowel/Comet/Braco |  |  |
| 24 | Dash fasteners |  | Hilti /Canco |  |  |
| 25 | Clamps |  | Chilly/Lovely/Dyena |  |  |
| 26 | Y Strainers |  | Zoloto/Leader / Kartar |  |  |
| 27 | Foot Valve |  | Zoloto/Leader / Kartar |  |  |
| 28 | Pump for Water Supply and Sump Pump |  | Ebara/Franklin/Grundfos |  |  |
| 29 | Split Coupled vertical in-line pump |  | Kirloskar, Grundfos, Armstrong/KSB |  |  |

Scope of Work, Technical Data Sheet, and Specification of the Item/s

| S. No. | DESCRIPTION OF ITEM (S) |  | UNIT | QTY |
| --- | --- | --- | --- | --- |
| (A) |
| 1 | SITC of MS Pipe |  |  |  |
|  | Supplying, fixing, testing, and commissioning of following sizes (NB) of ISI marked M.S pipe. C class including cutting, threading, welding etc. and providing all fittings e.g. elbows, reducers, clamps, hangers, flanges, gaskets, nuts, bolts and washers etc. including painting of pipes and fittings with red paint over a coat of ready mixed primer, both of approved quality and shade including cutting holes and chases in brick or RCC walls/slabs and making good the same etc. complete in all respect as required.(Make : TATA/JINDAL/SURYA) |  |  |  |
| a. | 150mm dia. |  | Mtrs | 150 |
| b. | 100mm dia |  | Mtrs | 50 |
| c. | 80 mm dia |  | Mtrs | 50 |
| 2 | SITC of Butterfly Valve / Gate valve |  |  |  |
|  | Providing and fixing of cast iron double flanged Butterfly Valve, wafer type PN1.6 IS:13095 complete with nuts and bolts rubber insertion all as required. (MAKE- UTTAM/ CASTLE/KARTAR/ ZOLOTO ) |  |  |  |
| a. | 150mm dia |  | Nos. | 5 |
| b. | 100 mm dia |  | Nos. | 2 |
| c. | 80 mm dia |  | Nos. | 1 |
| 3 | SITC of Cast Iron Flanged Non Return Valve |  |  |  |
|  | Providing and fixing of cast iron double flanged type non-return valve PN 1.6 IS:13095 complete with nut and bolts rubber insertion as required: (Wafer type) (MAKE- UTTAM/ CASTLE/KARTAR) |  |  |  |
| a) | 150mm dia |  | Nos. | 1 |
| 4 | SITC of EXPANSION ELBOWS |  |  |  |
|  | 150 mm dia |  | Nos | 5 |
|  | 100 mm dia. |  | Nos | 2 |
|  | 80 mm dia, |  | Nos | 2 |
| 5 | SITC of Fire Hose |  |  |  |
|  | Supplying, Installation, Testing and Commissioning 100% synthetic flax canvas Non-percolating FIRE hose I.S.I marked 63mm diax15m long with Gun metal male & female couplings (ISI marked) bound & riveted to hose pipes with copper rivets and copper wire as required. (MAKE- SAFEGUARD/ PADMINI/GUARDS/OMEX/FALCON) |  | Nos | 10 |
| 6 | SITC of Short Branch Pipe |  |  |  |
|  | Supplying, Installation, Testing and Commissioning Gun metal l 63mm dia. Short Branch Pipe (ISI marked) with 20mm dia nozzle as required. (MAKE- SAFEGUARD/GEETECH/GUARDS/OMEX/FALCON) |  | Nos | 5 |
| 7 | SITC of Single Headed G.M. Oblique Hydrant Landing Valve |  |  |  |
|  | Supplying, installation, testing and commissioning of single headed Gun metal, ISI marked oblique hydrant landing valve with 80mm dia flanged inlet & 63mm dia instanteous type female outlet complete with A.B.S. plastic cap and chain, twist release type lug and all accessories complete as required. (MAKE- SAFEGUARD/GEETECH/GUARDS/FALCON) |  | Nos | 5 |
| 8 | SITC of Weatherproof Cabinet for Hose |  |  |  |
|  | Supplying, installation, testing and commissioning of weather proof cabinet for hose fabricated out of 1.8 mm thickness M.S. sheet complete with glass in front having locking arrangement, suitable to accommodate all the necessary pipes (2 nos 15 mtr RRL & 1 no. branch pipe), accessories, fittings etc. including sign writing etc. as per drawing and specifications attached. Complete with suitable size MS stand |  | Nos | 5 |
| 9 | Supply & fixing of MS Clampl support for Ring Main Pipe as per details in the drawing include required size fastener, painting the same with 1 coat of primer and 2 coats of synthetic enamel. |  | Nos | 300 |
| 10 | Providing suitable size Brick masonry support structure for giving support to MS pipe Fire Ring main |  | Nos | 80 |
| 11 | Preparation of required set of drawings for submission to state Govt / Fire department for taking NOC , Job include the necessary liasioning work with the state Fire services / Municipal office complete as required |  | Job | 1 |
|  | Total (A) |  |  |  |
| (B) | CONVENTIONAL FIRE ALARM SYSTEM |  |  |  |
| 1 | SITC of conventional type Photo electric type Smoke Detector as per specifications complete with back box and original base. (Make: - GST/Morley/AGNI (EN-LPCB Approval) |  | Nos | 35 |
| 2 | SITC of Manual Call Points complete with MS / ABS body, LED indicator,etc. as per specifications. (Make: - GST/Morley/AGNI (EN-LPCB Approval) |  | Nos | 35 |
| 3 | SITC of 24 volt operated Sounder cum flasher complete (Make :- GST/Morley/AGNI (EN-LPCB Approval ) |  | Nos. | 15 |
| 4 | SITC of Microprocessor based 8 zone Fire Alarm Control Panels with 2 no’s 12V 7AH battrey & inbuilt battrey charger complete as required (Make :- GST/Morley/AGNI (EN-LPCB Approval ) |  | Nos | 2 |
| 5 | Supply & fixing of, 2 Core 1.5 sqmm PVC, flexible copper conductor FRLS cable for connection to fire detectors, call points and hooters in series including making the connection with necessary glands ( Make Havells/ KEI/ Ramson/Ecko/ Polycab/ Kalinga/Natonal ) |  | Mtrs | 1500 |
| 6 | Supply & fixing of Photolouminiscent type EXIT signages on 3 mm acrylic sheet of size 12 x 6 inch at various location complete with fixing arrangement of waal / ceiling as required |  | Nos | 35 |
| 7 | Providing & fixing required FIRE Safety & Industrial safety charts as per the requirement of Fire & safety department |  | Nos | 4 |
|  | Total (B) |  |  |  |
| (C ) | FIRE EXTINGUISHERS & FIRE BUCKETS |  |  |  |
| 1 | Supply, Installation, testing, commissioning of ISI marked (IS:15683) Portable fire extinguisher, of 4.5 kg capacity Carbon-dioxide type flat base including valve, discharge hose of not less than 10 mm dia 1m long & complete in all respects including initial fill with CO2 gas confirming to IS: 15683 filled and wall suspension bracket.all respect. (Make: SAFEX/OMEX/ FALCON/MINIMAX/Lifegurad) |  | Nos | 28 |
| 2 | Supplying and fixing of ABC powder-based MAP 70% Fire Extinguishers 6.00 Kg. Capacity with 5 years warranty, which will works for A,B&C classes of fire, easy snap safty seal ,state -of -the- art magnetic pressure gauge, Instalert, controllable discharge mechanism, EPDM rubber hose pipe. Conforms to ISI standards IS:15683 (Make: SAFEX/OMEX/ FALCON/MINIMAX/Lifegurad) |  | Nos. | 28 |
| 3 | SITC of Fire Buckets 4 nos with round botom made out of MS / GI sheet painted with Fire red colour complete with Fire bucket stand having hanging capacity of 4 buckets |  | Set | 4 |

Commercial Bid: (in separate sealed envelope)

| The LNM Institute of Information Technology |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Name of the work: BH-4 T2 of Institute Fire System BOQ |  |  |  |  |  |
| S. No. | DESCRIPTION OF ITEM (S) | UNIT | QTY | Rate (Rs.) | Amount (Rs.) |
| (A) | Fire Fighting System |  |  |  |  |
| 1 | SITC of MS Pipe |  |  |  |  |
|  | Supplying, fixing, testing, and commissioning of following sizes (NB) of ISI marked M.S pipe. C class including cutting, threading, welding etc. and providing all fittings e.g. elbows, reducers, clamps, hangers, flanges, gaskets, nuts, bolts and washers etc. including painting of pipes and fittings with red paint over a coat of ready mixed primer, both of approved quality and shade including cutting holes and chases in brick or RCC walls/slabs and making good the same etc. complete in all respect as required. Road crossing with repairing, Soil digging , filling, and wrapping the pipe in ANTI CORROSION tapes include all work as per site requirement. (Make : TATA/JINDAL/SURYA) |  |  |  |  |
| a. | 150mm dia. | Mtrs | 150 |  |  |
| b. | 100mm dia | Mtrs | 50 |  |  |
| c. | 80 mm dia | Mtrs | 50 |  |  |
| 2 | SITC of Butterfly Valve / Gate valve |  |  |  |  |
|  | Providing and fixing of cast iron double flanged Butterfly Valve, wafer type PN1.6 IS:13095 complete with nuts and bolts rubber insertion all as required. (MAKE- UTTAM/ CASTLE/KARTAR/ ZOLOTO ) |  |  |  |  |
| a. | 150mm dia | Nos. | 5 |  |  |
| b. | 100 mm dia | Nos. | 2 |  |  |
| c. | 80 mm dia | Nos. | 1 |  |  |
| 3 | SITC of Cast Iron Flanged Non Return Valve |  |  |  |  |
|  | Providing and fixing of cast iron double flanged type non-return valve PN 1.6 IS:13095 complete with nut and bolts rubber insertion as required: (Wafer type) (MAKE- UTTAM/ CASTLE/KARTAR) |  |  |  |  |
| a) | 150mm dia | Nos. | 1 |  |  |
| 4 | SITC of EXPANSION ELBOWS |  |  |  |  |
|  | 150 mm dia | Nos | 5 |  |  |
|  | 100 mm dia. | Nos | 2 |  |  |
|  | 80 mm dia, | Nos | 2 |  |  |
| 5 | SITC of Fire Hose |  |  |  |  |
|  | Supplying, Installation, Testing and Commissioning 100% synthetic flax canvas Non-percolating FIRE hose I.S.I marked 63mm diax15m long with Gun metal male & female couplings (ISI marked) bound & riveted to hose pipes with copper rivets and copper wire as required. (MAKE- SAFEGUARD/ PADMINI/GUARDS/OMEX/FALCON) | Nos | 10 |  |  |
| 6 | SITC of Short Branch Pipe |  |  |  |  |
|  | Supplying, Installation, Testing and Commissioning Gun metal l 63mm dia. Short Branch Pipe (ISI marked) with 20mm dia nozzle as required. (MAKE- SAFEGUARD/GEETECH/GUARDS/OMEX/FALCON) | Nos | 5 |  |  |
| 7 | SITC of Single Headed G.M. Oblique Hydrant Landing Valve |  |  |  |  |
|  | Supplying, installation, testing and commissioning of single headed Gun metal, ISI marked oblique hydrant landing valve with 80mm dia flanged inlet & 63mm dia instanteous type female outlet complete with A.B.S. plastic cap and chain, twist release type lug and all accessories complete as required. (MAKE- SAFEGUARD/GEETECH/GUARDS/FALCON) | Nos | 5 |  |  |
| 8 | SITC of Weatherproof Cabinet for Hose |  |  |  |  |
|  | Supplying, installation, testing and commissioning of weather proof cabinet for hose fabricated out of 1.8 mm thickness M.S. sheet complete with glass in front having locking arrangement, suitable to accommodate all the necessary pipes(2 nos 15 mtr RRL & 1 no. branch pipe), accessories, fittings etc. including sign writing etc. as per drawing and specifications attached. Complete with suitable size MS stand | Nos | 5 |  |  |
| 9 | Supply & fixing of MS Clampl support for Ring Main Pipe as per details in the drawing include required size fastener, painting the same with 1 coat of primer and 2 coats of sysnthetic enamel. | Nos | 300 |  |  |
| 10 | Providing suitable size Brick masonry/ RCC support structure for giving support to MS pipe Fire Ring main | Nos | 80 |  |  |
| 11 | Preparation of required set of drawings for submission to state Govt / Fire department for taking NOC , Job include the necessary liasioning work with the state Fire services / Municipal office complete as required, NOC renewal work include. | Job | 1 |  |  |
|  | Total (A) |  |  |  |  |
| (B) | CONVENTIONAL FIRE ALARM SYSTEM |  |  |  |  |
| 1 | SITC of conventional type Photo electric type Smoke Detector as per specifications complete with back box and original base. (Make: - GST/Morley/AGNI (EN-LPCB Approval) | Nos | 35 |  |  |
| 2 | SITC of Manual Call Points complete with MS / ABS body, LED indicator,etc. as per specifications. (Make: - GST/Morley/AGNI (EN-LPCB Approval) | Nos | 35 |  |  |
| 3 | SITC of 24 volt operated Sounder cum flasher complete (Make :- GST/Morley/AGNI (EN-LPCB Approval ) | Nos. | 15 |  |  |
| 4 | SITC of Microprocessor based 8 zone Fire Alarm Control Panels with 2 nos 12V 7AH battrey & inbuilt battrey charger complete as required (Make :- GST/Morley/AGNI (EN-LPCB Approval ) | Nos | 2 |  |  |
| 5 | Supply & fixing of, 2 Core 1.5 sqmm PVC, flexible copper conductor FRLS cable for connection to fire detectors, call points and hooters in series including making the connection with necessary glands ( Make Havells/ KEI/ Ramson/Ecko/ Polycab/ Kalinga/Natonal ) | Mtrs | 1500 |  |  |
| 6 | Supply & fixing of Photolouminiscent type EXIT signages on 3 mm acrylic sheet of size 12 x 6 inch at various location complete with fixing arangement of waal / ceiling as required | Nos | 35 |  |  |
| 7 | Providing & fixing required FIRE Safety & Industrial safety charts as per the requirement of Fire & safety department | Nos | 4 |  |  |
|  | Total (B) |  |  |  |  |
| (C ) | FIRE EXTINGUISHERS & FIRE BUCKETS |  |  |  |  |
| 1 | Supply, Installation, testing, commissioning of ISI marked (IS:15683) Portable fire extinguisher, of 4.5 kg capacity Carbon-dioxide type flat base including valve, discharge hose of not less than 10 mm dia 1m long & complete in all respects including initial fill with CO2 gas confirming to IS: 15683 filled and wall suspension bracket.all respect. (Make: SAFEX/OMEX/ FALCON/MINIMAX/Lifegurad) | Nos | 28 |  |  |
| 2 | Supplying and fixing of ABC powder-based MAP 70% Fire Extinguishers 6.00 Kg. Capacity with 5 years warranty, which will works for A,B&C classes of fire, easy snap safty seal ,state -of -the- art magnetic pressure gauge, Instalert, controllable discharge mechanism,EPDM rubber hose pipe. Conforms to ISI standards IS:15683 (Make: SAFEX/OMEX/ FALCON/MINIMAX/Lifegurad) | Nos. | 28 |  |  |
| 3 | SITC of Fire Buckets 4 nos with round botom made out of MS / GI sheet painted with Fire red colour complete with Fire bucket stand having hanging capacity of 4 buckets | Set | 4 |  |  |
|  | Total (C) |  |  |  |  |
|  | Total ( A + B +C) |  |  |  |  |
|  | GST@18% |  |  |  |  |
|  | Miscellaneous |  |  |  |  |
|  | Grand Total |  |  |  |  |

- Taxes like GST shall be clearly mentioned. If nothing is mentioned, these charges shall be deemed included.

- If the supplier does not have a particular item offered in the tender or a different make is being proposed by him, the same should be highlighted/mentioned especially by him.

- The prices should include all (Packing, forwarding, Transit Insurance, Transportation Loading/unloading, Installation etc.). Loading/unloading up to 50 Mtr. shall be done by the supplier.

- Bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- Bid should be valid for a minimum period of 30 days. The Change in prices shall not be accepted within the validity period.

- The LNMIIT reserves the right to reject any quotation(s) without assigning any reasons.

- Payment terms shall be decided mutually.

- There should not be any conflict of interest (Declaration to be submitted by the Vendor).

- Bid should be on the company’s letterhead and should submit their bid in the LNMIIT format only.

- Item/Service not supplied by the supplier/service provider should be mentioned separately.

- Vendor should provide a photocopy of the cheque/cancelled cheque while presenting the Invoice to LNMIIT.

- Pre-bid meeting and pre-bid site visit is mandatory before quoting the rate in the tender to clear up any confusion regarding project details, the scope of work, and solicitation of documents.

- In case of any query, please contact.

Mr. Ashok Salecha,

Finance Officer finanace@lnmiit.ac.in,

Mobile number-9413341246

Request kindly attach your company Profile.

All charges applicable shall be clearly mentioned with the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final, and nothing extra shall be paid extra.

Signature with seal