TENDER DOCUMENT

for

Supply, Installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricate Stand

From

The LNM institute of Information Technology

Rupa Ki Nangal, Post -  Sumel, Via – Jamdoli,

Jaipur – 302 031 (Raj.) INDIA

Tender Document

Sealed tenders are invited for the providing equipment’s for “Supply, installation, testing and commissioning of 10 KVA Single Phase online UPS System and SMF UPS Battery 26 ah/12V with MS Fabricated Stand with all accessories, as per the specifications and the details provided. Sealed offers can be sent to the following address by Speed-post/Registered Post/By-hand (but not by Courier).

Finance Officer

The LNM Institute of Information Technology,

Gram – Rupa Ki Nangal, Post – Sumel,

Via – Jamdoli, Jaipur- 302031

www.lnmiit.ac.in

Bidders can also submit their offer/s via email with password protected document/file at the below mentioned email IDs before 05:00 PM on 31/03/2024.

The Password protected document/file along with password to be sent at the email id: Chairman-PCC subcommittee chairman.pcc.projects@lnmiit.ac.in

Bid Process:

Technical & commercial details of the offer shall be enclosed in two separate envelopes, duly marked as “Technical bid for Supply and Installation of UPS” and “Commercial Bid for Supply and Installation of UPS ”. Both Envelopes shall be enclosed in a single envelope bearing the heading “Bid for Supply and Installation of Window AC”.

Bids are liable to be rejected if any or both of the technical or commercial offers are found in open condition or required information is not found with the offer.

Technical Bid: (in separate sealed envelope)

Technical Bid

The job of supply and installation of 10 KVA UPS   system complete with all accessories and fittings for proper air-conditioning of Hostels rooms.

While submitting quotations, the following documents may kindly be attached (separate sheet, if required).

- Name & address of the firm

Telephone No.

Email ID

- Type of firm:(Sole Proprietorship/Partnership/Ltd. Co/Pvt. Ltd./Others)

- PAN No.(attach copy)

- GST No. (attach copy)

- Details of similar works carried out during FY 2020-21, 2021-22, 2022-23. (attach copies)

| Year | Name of the Organization | Work order ref. and Date |
| --- | --- | --- |

Name and signature of Vendor

Seal

Date:

Place:

Technical Specifications

| Technical Specifications of UPS System |  |  |
| --- | --- | --- |
| S/No | Specification | Parameter requirements |
|  | Make | Numeric/APC/Socomec |
| 1. | UPS Capacity | 10 kVA |
| 2. | Technology | a. True online double conversion b. IGBT based rectifier & inverter c. Inbuilt PRS kit for Parallel Option in future |
| 3. | Input Parameters: |  |
| a. | Voltage | 230 VAC, 1 Phase |
| b. | Voltage Range | 110V to 300 VAC based on load level |
| c. | Frequency | 50 Hz |
| d. | Power Factor at rated load | Unity at full load |
| e. | Current Harmonic Distortion | Less than 10% |
| 4. | Output Parameters: |  |
| a. | Voltage | 220/230/240 VAC +/ - 1%, 1 Phase |
| b. | Frequency | 50 Hz +/- 0.25 Hz (in Battery Mode) +/- 6% (in Sync) |
| c. | THD v | < 2 % for Linear Load ; < 5 % for Non Linear Load |
| d. | Overload rating | 105 to 109 % - 10 min ; 110 to 129 % - 60 sec ; 150 % - 10 seconds |
| e. | Output waveform | Pure sinewave |
| f. | Crest Factor | 3 : 1 |
| g. | Output Power Factor | 0.9 |
| h. | Over all Efficiency | >93% without Transformer |
| 5. | Battery Parameters: |  |
| a. | Batteries Type ( 12V VRLA) | Sealed Maintenance Free Batteries ( Exide ) |
| e. | Backup Time | 30 Mins. |
| f. | DC Voltage | 192 VDC |
| h. | Battery Rack | Battery Rack / Stand |
| i. | Transfer time | UPS to Battery Mode : 0 ms |
| j | Three Stage Charger | Constant Voltage / Constant Current / Float Charging with Temperature Compensated Charger |
| k | Charging Capacity | 10 % of the Battery AH Capacity |
| 6. | Bypass: |  |
|  | Static Bypass | Required (Inbuilt) |
|  | Transfer time | < 4 ms in Sync Mode |
|  | Bypass parameter configurable via front panel | Required |
|  | Manual Bypass | Required (Inbuilt) |
| 7. | LCD Display / Alarm / Protection |  |
| a. | Metering Data |  |
|  |  | Input Voltage |
|  |  | Input Frequency |
|  |  | Output Voltage |
|  |  | Output Frequency |
|  |  | Output Power in Watts |
|  |  | Output Current |
|  |  | Load Level in % |
|  |  | Battery Voltage |
|  |  | Battery Level |
|  |  | Temperature |
|  |  | Event Log |
|  |  | Battery Test |
| b. | Status Information Data |  |
|  |  | Normal |
|  |  | Bypass |
|  |  | Battery |
|  |  | Fault |
|  |  | Converter Mode |
|  |  | Eco Mode |
|  |  | Bypass Mode |
|  |  | Battery Mode |
| c. | Fault / Waring Indication |  |
|  |  | Over Load |
|  |  | Charger Fail |
|  |  | Inverter Fault |
|  |  | Over Temperature |
|  |  | Short Circuit |
|  |  | DC low / High |
|  |  | Output Low / High |
|  |  | Fan Fail |
|  |  | Battery Disconnected |
| d. | Protection Required | Input High / Low |
|  |  | Over Load |
|  |  | Short Circuit |
|  |  | Over Temperature |
|  |  | Battery Over Charge |
|  |  | Battery Deep Discharge |
| e. | Audible Alarm | Battery Mode |
|  |  | Low Battery |
|  |  | Fault |
|  |  | Over Load |
|  |  | Bypass Mode |
| 8. | Other Features: |  |
| a. | Communication Port | RS 232 & USB |
| b. | Cold Start | Required |
| c. | Auto Restart | Required |
| d. | EPO | Required |
| e. | Generator Compatibility | Required |
| f. | SNMP Card | Optional |
| g. | Operating Temperature | 0 to 45 Deg C without derating |
| h. | Storage Temperature | 0 to 60 Deg C |
| i. | Humidity | upto 95 % |
| j. | Altitude | < 1000 meters |
| 9. | Connection |  |
|  | Input | Terminal Block |
|  | Output | Terminal Block |
|  | Battery | Terminal Block |
| 10. | Credential / Reports |  |
|  | ISO 9001 2015 | Copies Required |
|  | ISO 14001 2004 | Copies Required |
|  | ISO 45001: 2018 | Copies Required |
|  | BIS Certificate | Copies Required |
|  | JIS 8702C for battery | Copies Required |
|  | Manufacturing facility | a. Make in India. b. OEM Minimum 10 Years presence in India. |
|  | Service facility | UPS manufactures should have not less than 200 service centers accross India. |
|  | Turn Over | Vendor should have turn over more than 300 crores |
| 11. | Warranty /After Sales Support |  |
|  | Service Support | Directly from OEM for UPS & Batteries Both |
|  | Warranty | Onsite 24 Months on UPS & Batteries |
|  | Numeric Authorized service center | Local Authorized service center in Jaipur |
|  | Authorized Supplier Certificate | Numeric |

Commercial/Financial Bid: (in separate sealed envelope)

Financial Bid

| S. No. | Particulars | Make | Qty. | UOM | Rate | Amount |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Supply, Instruction, testing and commissioning of 10 KVA Single Phase online UPS System with two-year warranty | Numeric/APC/Socomec | 1 | Nos. |  |  |
| 1 | SMF UPS Battery 26 ah/12V with MS Fabricate Stand | Exide/ Amaron | 16 | Nos. |  |  |
|  | Total |  |  |  |  |  |
|  | GST_______ |  |  |  |  |  |
| TOTAL (including taxes) |  |  |  |  |  |  |

- Taxes should be clearly mentioned. If nothing is mentioned, these charges shall be deemed included in the prices offered.

- Any packing, forwarding and transit insurance charges are to be clearly specified. If nothing is mentioned, these charges shall be deemed included in the prices offered.

- The bid should be submitted for F.O.R delivery at the destination i.e. The LNM Institute of Information Technology, Gram – Rupa Ki Nangal, Post – Sumel, Via – Jamdoli, Jaipur- 302031

- The terms and conditions for the supply, delivery, installation, and commissioning should be very clearly indicated in the bid documents.

- Bid should be valid for a minimum period of 30 days.

- Please indicate the execution period.

- The LNMIIT reserves the right to reject any quotation(s) in full or part, without assigning any reasons.

- Payment terms shall be clearly specified with the bid document. However, the same may be further negotiated.

- Payment to be made for the final quantity executed on site and verified with our project team.

- In case of any query, please contact.

1.Mr. Ashok Salecha, Finance Officer finanace@lnmiit.ac.in,

mobile number-9413341246

2. Mr. Devendra Chaudhari, Estate Manager, estate.manager@lnmiit.ac.in

Request kindly attach your company profile.

All charges applicable shall be clearly mentioned in the offer. If nothing is mentioned in the offer, the quoted price shall be treated as final and nothing extra shall be paid extra.

Signature with seal